- ОХРАНА ОКРУЖАЮЩЕЙ СРЕДЫ

- УДК 628.179.2

Аксенов В. И., Галкин Ю. А. Безотходная замкнутая система производственного водоснабжения ООО «ВИЗ-Сталь» 4

В. И. АКСЕНОВ1, Ю. А. ГАЛКИН2

1 Аксенов Валентин Иванович, кандидат технических наук, профессор кафедры «Водное хозяйство и технология воды», лауреат Государственной премии СССР, Уральский федеральный университет имени первого Президента России Б. Н. Ельцина

620002, Россия, г. Екатеринбург, ул. Мира, 17, тел.: (343) 375-93-19, e-mail: ni.7@mail.ru

2 Галкин Юрий Анатольевич, доктор технических наук, генеральный директор ООО «Научно-проектная фирма ЭКО-ПРОЕКТ», профессор кафедры «Водное хозяйство и технология воды», Уральский федеральный университет имени первого Президента России Б. Н. Ельцина

620075, Россия, г. Екатеринбург, Первомайская ул., 15, оф. 900, тел.: (343) 283-01-04, e-mail: mail@eco-project.ru

Описана история создания первой в черной металлургии замкнутой безотходной системы производственного водоснабжения комплекса цеха холодной прокатки трансформаторной стали на Верх-Исетском металлургическом заводе (г. Екатеринбург). Поскольку строительство цеха планировалось в центре полуторамиллионного города, на берегу Верх-Исетского пруда, вблизи питьевого водозабора, требовалось создать такую систему водоснабжения, которая бы полностью исключала попадание сточных вод и отходов от их обработки в окружающую среду. Первым шагом в ее создании стало внедрение купоросной установки для очистки экологически опасных отходов – отработанных высококонцентрированных травильных растворов. Далее была разработана флотационная технология очистки маслоэмульсионных сточных вод. В экспериментальных исследованиях проверялась эффективность применения осветлителей с взвешенным осадком в схемах очистки сточных вод от пальмового масла оборотной воды стана холодной прокатки. Наибольшее внимание уделялось техническим решениям по переработке отходов, полученных при очистке загрязненных технологических вод. Создана установка для сжигания маслоотходов. Осадки сточных вод сначала обезвоживались на фильтр-прессах, затем подвергались сушке. Разработка выпарной установки для термического обессоливания продувочных вод оборотных циклов цеха холодной прокатки трансформаторной стали и сточных вод химической водоочистки заводской теплоэлектроцентрали позволила обеспечить замкнутость (бессточность) всей системы производственного водоснабжения. Опыт Верх-Исетского металлургического завода, особенно в части переработки твердых отходов и обессоливания сточных вод, был использован при создании эффективных систем водоснабжения многих предприятий разных отраслей промышленности, в том числе при реконструкции системы водоснабжения Новолипецкого металлургического комбината.

Ключевые слова: черная металлургия, сточные воды, отработанные травильные растворы, бессточная система водоснабжения, обессоливание, окружающая среда.

- СПИСОК ЛИТЕРАТУРЫ

- Аксенов В. И. Замкнутые системы водного хозяйства металлургических предприятий. – М.: Металлургия, 1983. 98 с.

- Ожиганов В. С., Иванцов Г. Б. Быль о чистой воде. – Свердловск: Средне-Уральское книжное издательство, 1985. 160 с.

- Яковлев С. В., Скирдов И. В., Швецов В. Н., Бондарев А. А., Андрианов Ю. Н.  Биологическая очистка производственных сточных вод: Процессы, аппараты и сооружения. – М.: Стройиздат, 1985. 208 с.

- Яковлев С. В., Карелин Я. А., Ласков Ю. М., Воронов Ю. В. Водоотводящие системы промышленных предприятий. – М.: Стройиздат, 1990. 511 с.

- Аксенов В. И., Беличенко Ю. П., Галкин Ю. А. Замкнутые системы водопользования на трубных предприятиях. – М.: Металлургия, 1987. 112 с.

- Пыриков А. Н., Вильданов С. К., Лиходиевский А. В., Мартынов Н. Н. Пути решения экологических проблем в черной металлургии // Сталь. 2008. № 5. С. 99–102.

- Галкин Ю. А. Инновационные технологии водоподготовки для основных переделов черной металлургии // Сталь. 2009. № 3. С. 92–93.

- Шебаршова И. М., Левашова Е. В., Таранин И. В., Ласьков С. А., Клещев Е. Г. Опыт освоения технологии регенерации соляной кислоты в псевдоожиженном слое // Сталь. 2013. № 9. С. 96–98.

- Галкин Ю. А. Технологическая модель сложных систем водного хозяйства промышленных предприятий и комплексов // Водоснабжение и санитарная техника. 2010. № 6. С. 27–31.

- Галкин Ю. А. Разработка и результаты применения отстойников-флокуляторов для очистки оборотной воды металлургических заводов России и Украины // Водоснабжение и санитарная техника. 2010. № 2. С. 5–9.

- Аксенов В. И., Архипова О. А., Сидорова И. А., Ничкова И. И. Создание замкнутых систем водоснабжения металлургических предприятий // Сталь. 2005. № 9. С. 83–85.

- Аксенов В. И., Ладыгичев М. Г., Ничкова И. И., Никулин В. А., Кляин С. Э., Аксенов Е. В. Водное хозяйство промышленных предприятий: Справочное издание. В 6 книгах. Книга 2. – М.: Теплотехник, 2005. 432 с.

- Алферова Л. А., Нечаев А. П. Замкнутые системы водного хозяйства промышленных предприятий, комплексов и районов. – М.: Стройиздат, 1984. 272 с.

- Ласкорин Б. Н., Громов Б. В., Цыганков А. П., Сенин В. Н. Безотходная технология в промышленности. – М.: Стройиздат, 1986. 160 с.

- Головных Н. В., Полонский С. Б., Шепелев И. И. Системы замкнутого и оборотного водоснабжения в алюминиевом производстве // Экология производства. 2008. № 3. С. 53–59.

- Багров О. Н., Антонов В. Н., Куликов Э. П., Смирнова О. В. Системы полного оборотного водоснабжения в цветной металлургии. – М.: Металлургия, 1978. 144 с.

- Левин Г. М., Пантелят Г. С., Вайнштейн И. А., Супрун Ю. М. Защита водоемов от загрязнения сточными водами предприятий черной металлургии. – М.: Металлургия, 1978. 216 с.

ENVIRONMENTAL PROTECTION

Aksenov V. I., Galkin Iu. A. Zero waste VIZ-Stal' LLC recycling system of industrial water supply 4

V. I. AKSENOV1, Iu. A. GALKIN2

1 Aksenov Valentin Ivanovich, PhD (Engineering), Professor, Laureate of USSR State Prize, Water Management and Technologies Department, Ural Federal University named after the First President of Russia B. N. Yeltsin

19 Mira str., 620002 Ekaterinburg, Russian Federation, tel.: +7 (343) 375-93-19, e-mail: ni.7@mail.ru

2 Galkin Iurii Anatol'evich, Doctor of Engineering, General Director, «EKO-PROEKT Research and Engineering Company» LLC, Professor, Water Management and Technologies Department, Ural Federal University named after the First President of Russia B. N. Yeltsin

15, office 900, Pervomaiskaia str., 620075 Ekaterinburg, Russian Federation, tel.: +7 (343) 283-01-04, e-mail: mail@eco-project.ru

The history of developing the first in metallurgy zero waste recycling system of industrial water supply of a transformer steel cold rolling plant at the Verkh-Isetsk steelworks (Ekaterinburg) is described. Since building the plant was planned in the centre of the city with the population of 1.5 million people on the bank of the Verkh-Isetsk pond near the drinking water intake it was required to design a system of industrial water supply with complete elimination of the wastewater and industrial wastes discharge into the environment. The first step of developing the system was retrofitting a vitriol unit for the removal of environmentally hazardous wastes – spent concentrated pickling plant liquor. Hereafter the flotation technology of oil emulsion wastewater treatment was developed. In the course of experimental studies the efficiency of using clarifiers with suspended sediment in the process of removing palm oil from recycled water of the cold rolling mill was investigated. Most attention was paid to the technical solutions of processing the wastes generated in the process of industrial wastewater treatment. The unit for oil waste incineration was designed. Wastewater sludge was initially dewatered in the filter-presses, and then dried. Designing an evaporation plant for thermal desalination of blowdown water of the closed-loop cycles of the transformer steel cold rolling plant and wastewater from the chemical treatment of the thermal power plant effluent provided for the zero discharge of the entire industrial water supply system. The experience of the Verkh-Isetsk steelworks, particularly in relation to processing solid wastes and wastewater desalination, was used in designing efficient water supply systems for various industries including the upgrade of the Novolipetsk steelworks water supply system.

Key words: steel industry, wastewater, spent pickling plant liquor, zero discharge water supply system, desalination, environment.

- REFERENCES

- Aksenov V. I. Zamknutye sistemy vodnogo khoziaistva metallurgicheskikh predpriiatii [Closed-loop water systems of steelworks. Moscow, Metallurgiia Publ., 1983, 98 p.].

- Ozhiganov V. S., Ivantsov G. B. Byl' o chistoi vode [True story about clean water. Sverdlovsk, Sredne-Ural'skoe Knizhnoe Izdatel'stvo Publ., 1985, 160 p.].

- Iakovlev S. V., Skirdov I. V., Shvetsov V. N., Bondarev A. A., Andrianov Iu. N. Biologicheskaia ochistka proizvodstvennykh stochnykh vod: Protsessy, apparaty i sooruzheniia [Biological treatment of industrial effluents: Processes, apparatus and facilities. Moscow, Stroiizdat Publ., 1985, 208 p.].

- Iakovlev S. V., Karelin Ia. A., Laskov Iu. M., Voronov Iu. V. Vodootvodiashchie sistemy promyshlennykh predpriiatii [Wastewater disposal systems of industrial enterprises. Moscow, Stroiizdat Publ., 1990, 511 p.].

- Aksenov V. I., Belichenko Iu. P., Galkin Iu. A. Zamknutye sistemy vodopol'zovaniia na trubnykh predpriiatiiakh [Zero discharge water systems at pipe mills. Moscow, Metallurgiia Publ., 1987, 112 p.].

- Pyrikov A. N., Vil'danov S. K., Likhodievskii A. V., Martynov N. N. [Environmental solution approaches in steel industry]. Stal', 2008, no. 5, pp. 99–102. (In Russian).

- Galkin Iu. A. [Innovative technologies of water treatment for basic steel converters]. Stal', 2009, no. 3, pp. 92–93. (In Russian).

- Shebarshova I. M., Levashova E. V., Taranin I. V., Las'kov S. A., Kleshchev E. G. [The experience of developing the technology of hydrochloric acid fluidized-bed regeneration]. Stal', 2013, no. 9, pp. 96–98. (In Russian).

- Galkin Iu. A. [Technological model of compound systems of water management at industrial enterprises and complexes]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2010, no. 6, pp. 27–31. (In Russian).

- Galkin Iu. A. [Development and the use of settling tank-flocculators for treatment of recirculated water at metallurgical works of Russia and Ukraine]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2010, no. 2, pp. 5–9. (In Russian).

- Aksenov V. I., Arkhipova O. A., Sidorova I. A., Nichkova I. I. [Designing zero discharge water supply systems for steelworks]. Stal', 2005, no. 9, pp. 83–85. (In Russian).

- Aksenov V. I., Ladygichev M. G., Nichkova I. I., Nikulin V. A., Kliain S. E., Aksenov E. V. Vodnoe khoziaistvo promyshlennykh predpriiatii [Industrial water management: Reference book. In 6 books. Book 2. Moscow, Teplotekhnik Publ., 2005, 432 p.].

- Alferova L. A., Nechaev A. P. Zamknutye sistemy vodnogo khoziaistva promyshlennykh predpriiatii, kompleksov i raionov [Zero discharge water management systems of industrial enterprises, complexes and regions. Moscow, Stroiizdat Publ., 1984, 272 p.].

- Laskorin B. N., Gromov B. V., Tsygankov A. P., Senin V. N. Bezotkhodnaia tekhnologiia v promyshlennosti [Waste free technology in industry. Moscow, Stroiizdat Publ., 1986, 160 p.].

- Golovnykh N. V., Polonskii S. B., Shepelev I. I. [Closed-loop and recycling water supply in aluminium production]. Ekologiia Proizvodstva, 2008, no. 3, pp. 53–59. (In Russian).

- Bagrov O. N., Antonov V. N., Kulikov E. P., Smirnova O. V. Sistemy polnogo oborotnogo vodosnabzheniia v tsvetnoi metallurgii [Complete recycling water supply in non-ferrous industry. Moscow, Metallurgiia Publ., 1978, 144 p.].

- Levin G. M., Panteliat G. S., Vainshtein I. A., Suprun Iu. M. Zashchita vodoemov ot zagriazneniia stochnymi vodami predpriiatii chernoi metallurgii [Protection of water bodies from steel industrial wastewater pollution. Moscow, Metallurgiia Publ., 1978, 216 p.].

ВОДОКАНАЛЫ РОССИИ

УДК 628.1.032

Васильева А. И., Кантор Л. И., Труханова Н. В., Мельницкий И. А. Полициклические ароматические углеводороды в воде водоисточников г. Уфы 12

А. И. ВАСИЛЬЕВА1, Л. И. КАНТОР2, Н. В. ТРУХАНОВА3, И. А. МЕЛЬНИЦКИЙ4

1 Васильева Алла Ильинична, кандидат химических наук, начальник отдела хроматографического анализа, Центральная химико-бактериологическая лаборатория, Центр аналитического контроля качества воды, МУП «Уфаводоканал»

450098, Россия, г. Уфа, Российская ул., 157/2, тел.: (347) 284-68-32, e-mail: vasall2007@mail.ru

2 Кантор Лев Исаакович, кандидат технических наук, технический директор, первый заместитель генерального директора, МУП «Уфаводоканал»

450098, Россия, г. Уфа, Российская ул., 157/2, тел.: (347) 284-13-63, e-mail: uwc@uwc.ufanet.ru

3 Труханова Наталья Владимировна, кандидат химических наук, начальник Центральной химико-бактериологической лаборатории, Центр аналитического контроля качества воды, МУП «Уфаводоканал»

450098, Россия, г. Уфа, Российская ул., 157/2, тел.: (347) 284-68-30, e-mail: uwc@uwc.ufanet.ru

4 Мельницкий Игорь Александрович, доктор химических наук, главный специалист по контролю качества воды, МУП «Уфаводоканал»

450098, Россия, г. Уфа, Российская ул., 157/2, тел.: (347) 284-68-30, e-mail: i_melnit@rambler.ru

Представлены результаты многолетнего мониторинга содержания полициклических ароматических углеводородов в питьевой воде и воде водоисточников на трех водозаборах города Уфы с использованием метода высокоэффективной жидкостной хроматографии с флуориметрическим детектированием. Исследован количественный и качественный состав полициклических ароматических углеводородов. Для оценки возможных источников поступления полициклических ароматических углеводородов в реку Уфу был проведен системный анализ относительного состава полициклических ароматических углеводородов по некоторым характерным соотношениям молярных концентраций индивидуальных соединений. Установлено преобладание петрогенных источников поступления полициклических ароматических углеводородов. Изучение сезонной динамики их содержания в воде реки Уфы показало, что максимальные концентрации наблюдаются в осенне-зимний период, а минимальные – в летний. При сравнении результатов проведенного исследования с опубликованными данными о загрязнении рек в Европе, Америке и Китае отмечено, что уровень содержания полициклических ароматических углеводородов в реке Уфе в основном ниже или близок к естественному природному фону. Для главного водоисточника г. Уфы мониторинг содержания полициклических ароматических углеводородов является объективной необходимостью, поскольку любое отклонение от фонового загрязнения или изменение качественного состава полициклических ароматических углеводородов может свидетельствовать об увеличении техногенной нагрузки на водоисточник, а значит, о риске ухудшения качества питьевой воды.

Ключевые слова: питьевая вода, полициклические ароматические углеводороды, пирогенный и петрогенный источники эмиссии углеводородов, отношение молярных концентраций.

СПИСОК ЛИТЕРАТУРЫ

- Суздорф А. Р., Морозов С. В., Кузубова Л. И., Аншиц Н. Н., Аншиц А. Г. Полициклические углеводороды в окружающей среде: источники, профили и маршруты превращения // Химия в интересах устойчивого развития. 1994. № 2. С. 511–540.

- Бродский Е. С. Типы полициклических ароматических углеводородов в окружающей среде и методы их определения: Тезисы докладов V Всероссийской конференции по анализу объектов окружающей среды «Экоаналитика–2003». – СПб, 2003. 32 с.

- Алексеева Т. А., Теплицкая Т. А. Спектрофлуориметрические методы анализа ароматических углеводородов в природных и техногенных средах. – Л.: Гидрометеоиздат, 1981. 216 с.

- Лахиджани Х. К., Немировская И. А., Красножон Г. Ф. Углеводороды в донных отложениях Иранского побережья Каспийского моря // Водные ресурсы. 1999. Т. 26. № 1. С. 104–107.

- Oros D. R., Ross J. R. M., Spies R. B., Mumley T. Polycyclic aromatic hydrocarbon contamination in San Francisco Bay: A 10-year retrospective of monitoring in an urbanized estuary // Environmental Research. 2007. № 105 (1). P. 101–118.

- Бродский Е. С., Лукашенко И. М., Калинкевич Г. А., Савчук С. А. Идентификация нефтепродуктов в объектах окружающей среды с помощью газовой хроматографии и хромато-масс-спектрометрии // Журнал аналитической химии. 2002. Т. 57. № 6. С. 592–596.

- Другов Ю. С., Родин А. А. Газохроматографическая идентификация загрязнений воздуха, воды и почвы. Практическое руководство. – СПб: Теза, 1999. 624 с.

- Руководство по обеспечению качества питьевой воды. Т. 1. Рекомендации. – Женева, ВОЗ, 2004. 121 с.

- Szabo Nagy A., Simon G., Van Vass I. Monitoring of polycyclic aromatic hydrocarbons (PAHS) in surface water of Hungarian upper section of the Danube river // Nova Biotechnologica et Chimica. 2012. № 11 (1). P. 27–35.

- Гирчыс Я., Цабан-Пабиан Б. Определение полициклических ароматических углеводородов в шахтных водах // Химия и технология воды. 2003. Т. 25. № 4. С. 350–357.

- Manoli E., Samara C., Konstantinou I., Albanis T. Polycyclic aromatic hydrocarbons in the bulk precipitation and surface waters of Northern Greece // Chemosphere. 2000. № 41. P. 1845–1855.

- Zhonghong Cao, Yuqiu Wang, Yongmin Ma, Ze Xu, Guoliang Shi, Yuanyi Zhuang, Tan Zhu. Occurrence and distribution of polycyclic aromatic hydrocarbons in reclaimed water and surface water of Tianjin, China // Journal of Hazardous Materials. 2005. V. 122. Issues 1–2. P. 51–59.

- Таранова Л. А., Иващенко Г. В. Биологическая деструкция полициклических ароматических углеводородов // Химия и технология воды. 2001. Т. 23. № 3. С. 177–197.

WATER AND WASTEWATER COMPANIES (VODOKANALS) IN RUSSIA

Vasil'eva A. I., Kantor L. I., Trukhanova N. V., Mel'nitskii I. A. Polycyclic aromatic hydrocarbons in the water sources of Ufa 12

A. I. VASIL'EVA1, L. I. KANTOR2, N. V. TRUKHANOVA3, I. A. MEL'NITSKII4

1 Vasil'eva Alla Il'inichna, PhD (Chemistry), Chief of Chromatographic Analysis Department, Central Chemical and Bacteriological Laboratory of the Water Quality Analytical Centre, «Ufavodokanal» MUE

157/2 Rossiiskaia str., 450098 Ufa, Russian Federation, tel.: +7 (347) 284-68-32, e-mail: vasall2007@mail.ru

2 Kantor Lev Isaakovich, PhD (Engineering), Technical Director, Vice General Director, «Ufavodokanal» MUE

157/2 Rossiiskaia str., 450098 Ufa, Russian Federation, tel.: +7 (347) 284-13-63, e-mail: uwc@uwc.ufanet.ru

3 Trukhanova Natal'ia Vladimirovna, PhD (Chemistry), Chief of the Central Chemical and Bacteriological Laboratory of the Water Quality Analytical Centre, «Ufavodokanal» MUE

157/2 Rossiiskaia str., 450098 Ufa, Russian Federation, tel.: +7 (347) 284-68-30, e-mail: uwc@uwc.ufanet.ru

4 Mel'nitskii Igor' Aleksandrovich, Doctor of Chemistry, Chief Specialist on Water Quality Control, «Ufavodokanal» MUE

157/2 Rossiiskaia str., 450098 Ufa, Russian Federation, tel.: +7 (347) 284-68-30, e-mail: i_melnit@rambler.ru

The results of long-term monitoring of the polycyclic aromatic hydrocarbons concentrations in drinking water and water sources at the three water intakes of Ufa with the use of high performance liquid chromatography with fluorimetric detection are presented. The qualitative and quantitative composition of polycyclic aromatic hydrocarbons has been investigated. The identification of possible sources of polycyclic aromatic hydrocarbons inflow into the Ufa River was carried out with the help of the system analysis of the relative composition of polycyclic aromatic hydrocarbons by some typical ratios of molar concentrations of separate compounds. The prevalence of petrogenic sources of polycyclic aromatic hydrocarbons inflow was found out. Studying the seasonal dynamics of their concentration in the Ufa River water showed that the maximum concentrations were observed during autumn-winter period, and minimum concentrations in summer. Comparing the results of the studies with the published data on river pollution in Europe, America, and China showed that the level of polycyclic aromatic hydrocarbons in the Ufa River was basically low or close to the natural background. Monitoring of polycyclic aromatic hydrocarbons in the major water source of Ufa is a reasonable requirement since any deviation from the background pollution level or any changes in the qualitative composition of polycyclic aromatic hydrocarbons can be indicative of the increased man-induced impact on the water source and consequently of the risk of the drinking water quality deterioration.

Key words: drinking water, polycyclic aromatic hydrocarbons, pyrogenic and petrogenic sources of hydrocarbons emission, molar concentration ratio.

REFERENCES

- Suzdorf A. R., Morozov S. V., Kuzubova L. I., Anshits N. N., Anshits A. G.  [Polycyclic aromatic hydrocarbons in environment: sources, profiles and transformation paths]. Khimiia v Interesakh Ustoichivogo Razvitiia, 1994, no. 2, pp. 511–540. (In Russian).

- Brodskii E. S. Tipy politsiklicheskikh aromaticheskikh uglevodorodov v okruzhaiushchei srede i metody ikh opredeleniia [Types of polycyclic aromatic hydrocarbons in environment and methods of their determination: Abstracts of the V «Ekoanalitika–2003» All-Russian Conference on the analysis of natural environments. St. Petersburg, 2003, 32 p.].

- Alekseeva T. A., Teplitskaia T. A. Spektrofluorimetricheskie metody analiza aromaticheskikh uglevodorodov v prirodnykh i tekhnogennykh sredakh [Spectrofluorimetric methods of analyzing aromatic hydrocarbons in natural and anthropogenic environments. Leningrad, Gidrometeoizdat Publ., 1981, 216 p.].

- Lakhidzhani Kh. K., Nemirovskaia I. A., Krasnozhon G. F. Uglevodorody v donnykh otlozheniiakh Iranskogo poberezh'ia Kaspiiskogo moria [Hydrocarbons in bottom sediments of the Iranian cost of the Caspian Sea]. Vodnye Resursy, 1999, v. 26, no. 1, pp. 104–107. (In Russian).

- Oros D. R., Ross J. R. M., Spies R. B., Mumley T. Polycyclic aromatic hydrocarbon contamination in San Francisco Bay: A 10-year retrospective of monitoring in an urbanized estuary. Environmental Research, 2007, no. 105 (1), pp. 101–118.

- Brodskii E. S., Lukashenko I. M., Kalinkevich G. A., Savchuk S. A. [Identification of oil products in environment with the help of gas chromatography and chromatography-mass spectrometry]. Zhurnal Analiticheskoi Khimii, 2002, v. 57, no. 6, pp. 592–596. (In Russian).

- Drugov Iu. S., Rodin A. A. Gazokhromatograficheskaia identifikatsiia zagriaznenii vozdukha, vody i pochvy. Prakticheskoe rukovodstvo [Gas chromatographic identification of air, water and soil pollutants. Practical guide. St. Petersburg, Teza Publ., 1999, 624 p.].

- Rukovodstvo po obespecheniiu kachestva pit'evoi vody. T. 1. Rekomendatsii [Guidelines for drinking-water quality. V. 1. Recommendations. Geneva, WHO, 2004, 121 p.].

- Szabo Nagy A., Simon G., Van Vass I. Monitoring of polycyclic aromatic hydrocarbons (PAHS) in surface water of Hungarian upper section of the Danube river. Nova Biotechnologica et Chimica, 2012, no. 11 (1), pp. 27–35.

- Girchys Ia., Tsaban-Pabian B. [Determining polycyclic aromatic hydrocarbons in mining water]. Khimiia i Tekhnologiia Vody, 2003, v. 25, no. 4, pp. 350–357. (In Russian).

- Manoli E., Samara C., Konstantinou I., Albanis T. Polycyclic aromatic hydrocarbons in the bulk precipitation and surface waters of Northern Greece. Chemosphere, 2000, no. 41, pp. 1845–1855.

- Zhonghong Cao, Yuqiu Wang, Yongmin Ma, Ze Xu, Guoliang Shi, Yuanyi Zhuang, Tan Zhu. Occurrence and distribution of polycyclic aromatic hydrocarbons in reclaimed water and surface water of Tianjin, China. Journal of Hazardous Materials, 2005, v. 122, issues 1–2, pp. 51–59.

- Taranova L. A., Ivashchenko G. V. [Biological destruction of polycyclic aromatic hydrocarbons]. Khimiia i Tekhnologiia Vody, 2001, v. 23, no. 3, pp. 177–197. (In Russian).

ЭКОНОМИЯ РЕСУРСОВ

УДК 628.179.34

Лернер А. Д., Инчагов А. Д., Слюсаренко А. В.  Пути снижения неучтенных расходов воды в системах коммунального водоснабжения 21

А. Д. ЛЕРНЕР1, А. Д. ИНЧАГОВ2, А. В. СЛЮСАРЕНКО3

1 Лернер Анатолий Давидович, кандидат технических наук, директор ООО «Дальневосточное предприятие Росводоканал», почетный строитель России, доцент кафедры «Гидравлика и водоснабжение», Тихоокеанский государственный университет

680013, Россия, г. Хабаровск, ул. Лермонтова, 38, тел.: (4212) 42-88-31, e-mail: lerner51@mail.ru

2 Инчагов Алексей Дмитриевич, ведущий инженер, ООО «Дальневосточное предприятие Росводоканал»

680013, Россия, г. Хабаровск, ул. Лермонтова, 38, тел.: (4212) 42-84-12, e-mail: inchagov@mail.ru

3 Слюсаренко Александр Владимирович, инженер отдела технического надзора, ООО «НИИКВОВ-САХАЛИН»

680013, Россия, г. Южно-Сахалинск, ул. Крюкова, 21, тел.: (914) 757-31-26, e-mail: ooo.olbik@gmail.com

При решении задач по повышению эффективности работы предприятий водопроводно-канализационного хозяйства большое значение приобретает снижение неучтенных расходов воды. Предложены новые подходы к оценке таких расходов с выделением из них физических потерь коммунального ресурса. Рассмотрен мировой опыт проведения мероприятий по снижению этих расходов на основе заключения контрактов с частными операторами исходя «из результата» реального достижения запланированного уменьшения удельной величины физических утечек и потерь воды. Дана сравнительная финансовая оценка мероприятий по строительству водозаборных сооружений и снижению неучтенных расходов. Рассмотрены экономические, социальные и политические факторы, препятствующие проведению работ по реальному снижению неучтенных расходов. Основной причиной нежелания коммунальных предприятий реализовывать программы снижения утечек является отсутствие материальных стимулов и штатно-организационной структуры. Сделан вывод о том, что к решению данной проблемы необходимо подключать собственников водопроводных систем, как правило, это органы местного самоуправления. Стоит иметь в виду, что снижение неучтенных расходов воды (в том числе с использованием контракта «из результата») не следует рассматривать как новую формулу для решения множества недочетов в работе предприятий водопроводно-канализационного хозяйства, поскольку эти недочеты являются следствием более фундаментальных основополагающих проблем. В свою очередь успешное решение задач водообеспечения населения без ввода новых мощностей может создать предпосылки для структурных реформ, которые необходимы для того, чтобы предприятия водопроводно-канализационного хозяйства и частный бизнес могли эффективно служить растущим потребностям в воде населения и промышленности.

Ключевые слова: неучтенный расход воды, управление коммунальным ресурсом, утечки воды, контракт «из результата», эффективность системы водоснабжения.

СПИСОК ЛИТЕРАТУРЫ

- Лернер А. Д. Неучтенные расходы в системах коммунального водоснабжения и водоотведения // Водоснабжение и санитарная техника. 2005. № 4. С. 9–12.

- Лернер А. Д. Обоснование нормативов потребления воды в городских системах Дальнего Востока // Водоснабжение и санитарная техника. 1998. № 8. С. 7–9.

- Лернер А. Д., Домнин К. В., Бойко С. В., Кочетова М. Г. Проблемы обоснования величин неучтенных расходов воды в системах водоснабжения и водоотведения // Водоснабжение и санитарная техника. 2012. № 7. С. 64–70.

- Храменков С. В., Примин О. Г. Проблемы и пути снижения потерь воды // Водоснабжение и санитарная техника. 2012. № 11. С. 31–37.

- Кингдом Б., Лимбергер Р., Марин Ф.: Пер. А. В. Слюсаренко.  Проблема снижения нереализуемой воды (НРВ) в развивающихся странах. Как частные фирмы могут помочь: обзор контрактов, заключенных на принципах оплаты из достигнутого результата. – М., 2006.

RESOURCE CONSERVATION

Lerner A. D., Inchagov A. D., Sliusarenko A. V. Ways to reduce unaccounted-for-water in public water supply systems 21

A. D. LERNER1, A. D. INCHAGOV2, A. V. SLIUSARENKO3

1 Lerner Anatolii Davidovich, PhD (Engineering), Director, «Far Eastern Enterprise Rosvodokanal» LLC, Honorary Builder of Russia, Assistant Professor, Hydraulics and Water Supply Department, Pacific National University

38 Lermontova str., 680013 Khabarovsk, Russian Federation, tel.: +7 (4212) 42-88-31, e-mail: lerner51@mail.ru

2 Inchagov Aleksei Dmitrievich, Leading Engineer, «Far Eastern Enterprise Rosvodokanal» LLC

38 Lermontova str., 680013 Khabarovsk, Russian Federation, tel.: +7 (4212) 42-84-12, e-mail: inchagov@mail.ru

3 Sliusarenko Aleksandr Vladimirovich, Engineer, Engineering Supervision Department, «NIIKVOV-SAKHALIN» LLC

21 Kriukova str., 680013 Yuzhno-Sakhalinsk, Russian Federation, tel.: +7 (914) 757-31-26, e-mail: ooo.olbik@gmail.com

In the process of improving the efficiency of water and wastewater services the reduction of unaccounted-for-water is of crucial importance. New approaches to the evaluation of these amounts with the selection of physical losses of the utilities resource are suggested. The world experience of taking measures on reducing these amounts by concluding contracts with private operators guided by the actual results of achieving the projected reduction of the specific physical leakages and water losses is considered. The comparative financial evaluation of the measures on constructing water intakes and reducing unaccounted-for-water is presented. Economic, social and political factors inhibiting the process of actual reducing unaccounted-for-water are considered. The main reason of public utilities being reluctant to take measures on the reduction of water leakages lies in the lack of financial incentives and organizational projects. It is concluded that the owners of the water supply systems, as a rule local authorities, shall be involved in solving the problem. It is worth keeping in mind that reducing unaccounted-for-water (including the use of performance-based service contracting) shall not be considered as a new formula for eliminating numerous shortcomings in the operation of water utilities, because these shortcomings result from the more fundamental problems. Successful public water supply management without introducing new capacities, in its turn, can predetermine the structural reforms required to ensure the efficient operation of water and wastewater services and private business in satisfying the growing water demand of population and industries.

Key words: unaccounted-for-water, utilities resource management, water leakages, performance-based service contracting, water supply efficiency.

REFERENCES

- Lerner A. D. [Unaccounted-for-losses in public water and wastewater systems]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2005, no. 4, pp. 9–12. (In Russian).

- Lerner A. D. [Substantiation of water consumption limits in Far Eastern public water supply systems]. Vodosnabzhenie i Sanitarnaia Tekhnika, 1998, no. 8, pp. 7–9. (In Russian).

- Lerner A. D., Domnin K. V., Boiko S. V., Kochetova M. G. [Justification of unaccounted-for-water in water supply and wastewater management systems]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2012, no. 7, pp. 64–70. (In Russian).

- Khramenkov S. V., Primin O. G. [The problems and ways to reduce water losses]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2012, no. 11, pp. 31–37. (In Russian).

- Kingdom B., Limberger R., Marin F.: Translated by A. V. Sliusarenko. Problema snizheniia nerealizuemoi vody (NRV) v razvivaiushchikhsia stranakh. Kak chastnye firmy mogut pomoch': obzor kontraktov, zakliuchennykh na printsipakh oplaty iz dostignutogo rezul'tata [The challenge of reducing non-revenue water (NRW) in developing countries. How the private sector can help: a look at performance-based service contracting. Moscow, 2006].

ВОДОПОДГОТОВКА

УДК 628.165:66.081.63

Первов А. Г., Андрианов А. П., Горбунова Т. П., Спицов Д. В., Юрчевский Е. Б. Удаление карбоната кальция из концентрата обратноосмотических установок путем кристаллизации на затравке 29

А. Г. ПЕРВОВ1, А. П. АНДРИАНОВ2, Т. П. ГОРБУНОВА3, Д. В. СПИЦОВ4, Е. Б. ЮРЧЕВСКИЙ5

1 Первов Алексей Германович, доктор технических наук, профессор кафедры «Водоснабжение», Московский государственный строительный университет

129337, Россия, Москва, Ярославское шоссе, 26, тел.: (499) 183-36-29, e-mail: waterlab@yandex.ru

2 Андрианов Алексей Петрович, кандидат технических наук, доцент кафедры «Водоснабжение», Московский государственный строительный университет

129337, Россия, Москва, Ярославское шоссе, 26, тел.: (499) 183-36-29, e-mail: alexei-waterlab@yandex.ru

3 Горбунова Тамара Петровна, инженер, ассистент кафедры «Водоснабжение», Московский государственный строительный университет

129337, Россия, Москва, Ярославское шоссе, 26, тел.: (499) 183-36-29, e-mail: tamusyav@mail.ru

4 Спицов Дмитрий Владимирович, кандидат технических наук, доцент кафедры «Водоснабжение», Московский государственный строительный университет

129337, Россия, Москва, Ярославское шоссе, 26, тел.: (499) 183-36-29, e-mail: dvs43000@rambler.ru

5 Юрчевский Евгений Борисович, доктор технических наук, главный научный сотрудник, ОКБ «Гидропресс»
142103, Россия, г. Подольск Московской области, ул. Орджоникидзе, 21, тел.: (4967) 54-25-16, e-mail: aquachim@yandex.ru

Описана технология удаления из концентрата обратноосмотических установок карбоната кальция путем его кристаллизации на затравке. Кристаллы затравки находятся во взвешенном состоянии в циркулирующем потоке концентрата. Благодаря осаждению карбоната кальция на затравке снижается общее солесодержание концентрата и достигается высокий расход фильтрата, что облегчает утилизацию концентрата. Для осуществления технологии используются мембранные аппараты с «открытым каналом», устойчивые к влиянию на процесс мембранного переноса осадков малорастворимых в воде солей и взвешенных веществ. Получение кристаллов затравки производится путем дозирования в концентрат раствора едкого натра. Частичное удаление выросших кристаллов затравки осуществляется отстаиванием после проведения гидравлических промывок мембран. С помощью экспериментальных графиков можно определить скорость процесса кристаллизации карбоната кальция в зависимости от состава исходной воды, количества внесенных кристаллов, величины выхода фильтрата. Предложена технологическая схема работы установки обратного осмоса в непрерывном режиме. Описаны методы технологического расчета установки: подбор количества циркулирующих кристаллов затравки, определение расхода едкого натра и размеров емкостей для отстаивания осадка карбоната кальция. Расчеты показали, что для проведения процесса кристаллизации карбоната кальция при работе установки обратного осмоса в непрерывном режиме в циркулирующий поток концентрата периодически дозируется раствор едкого натра в количестве, составляющем не более 5% от его стехиометрического количества, требуемого для осаждения того же количества карбоната кальция из исходной воды.

Ключевые слова: стабилизация воды, обратноосмотическая установка, концентрат, кристаллизация карбоната кальция, кристаллы затравки, утилизация концентрата.

СПИСОК ЛИТЕРАТУРЫ

- Апельцин И. Э., Клячко В. А. Опреснение воды. – М.: Стройиздат, 1968. 224 С.

- Harries R. C. A field trial of seeded reverse osmosis for the desalination of a scaling-type mine water // Desalination. 1985. № 56. P. 227–236.

- Herrigel H. R. The seeded reverse osmosis process field testing: 12-th Annual Conference on Water Supply Improvement Association. Orlando, Florida, USA, May 13–18, 1984. Technology Proceedings. V. 1. Sess. 1–6.

- Первов А. Г., Андрианов А. П., Юрчевский Е. Б. Совершенствование конструкций мембранных аппаратов // Водоснабжение и санитарная техника. 2009. № 7. С. 62–68.

- Первов А. Г., Рудакова Г. Я., Ефремов Р. В. Разработка программ для технологического расчета систем обратного осмоса и нанофильтрации с использованием реагентов «Аминат» // Водоснабжение и санитарная техника. 2009. № 7. С. 21–29.

- Первов А. Г., Козлова Ю. В., Андрианов А. П., Мотовилова Н. Б. Разработка технологии очистки поверхностных вод с помощью нанофильтрационных мембран // Критические технологии. Мембраны. 2006. № 1 (29). С. 20–33.

- Первов А. Г., Андрианов А. П., Горбунова Т. П., Юрчевский Е. Б. Технология утилизации концентрата установок обратного осмоса в системах водоподготовки // Водоснабжение и санитарная техника. 2012. № 8. С. 20–26.

- Первов А. Г., Ефремов Р. В., Спицов Д. В., Андрианов А. П., Горбунова Т. П. Мембранные методы в питьевом водоснабжении: подбор мембран, прогноз качества воды, утилизация концентрата // Водоснабжение и санитарная техника. 2013. № 6. С. 15–21.

WATER TREATMENT

Pervov A. G., Andrianov A. P., Gorbunova T. P., Spitsov D. V., Iurchevskii E. B. Removing calcium carbonate from reverse osmosis concentrate by crystallization with seeding agent 29

A. G. PERVOV1, A. P. ANDRIANOV2, T. P. GORBUNOVA3, D. V. SPITSOV4, E. B. IURCHEVSKII5

1 Pervov Aleksei Germanovich, Doctor of Engineering, Professor, Department of Water Supply, Moscow State University of Civil Engineering

26 Iaroslavskoe Hwy., 129337 Moscow, Russian Federation, tel.: +7 (499) 183-36-29, e-mail: waterlab@yandex.ru

2 Andrianov Aleksei Petrovich, PhD (Engineering), Assistant Professor, Department of Water Supply, Moscow State University of Civil Engineering

26 Iaroslavskoe Hwy., 129337 Moscow, Russian Federation, tel.: +7 (499) 183-36-29, e-mail: alexei-waterlab@yandex.ru

3 Gorbunova Tamara Petrovna, Engineer, Assistant, Department of Water Supply, Moscow State University of Civil Engineering

26 Iaroslavskoe Hwy., 129337 Moscow, Russian Federation, tel.: +7 (499) 183-36-29, e-mail: tamusyav@mail.ru

4 Spitsov Dmitrii Vladimirovich, PhD (Engineering), Assistant Professor, Department of Water Supply, Moscow State University of Civil Engineering

26 Iaroslavskoe Hwy., 129337 Moscow, Russian Federation, tel.: +7 (499) 183-36-29, e-mail: dvs43000@rambler.ru

5 Iurchevskii Evgenii Borisovich, Doctor of Engineering, Chief Research Fellow, «Gidropress» Experimental Design Bureau
21 Ordzhonikidze str., 142103 Podolsk, Moscow Area, Russian Federation, tel.: +7 (4967) 54-25-16, e-mail: aquachim@yandex.ru

The technology of removing calcium carbonate from reverse osmosis concentrate in the process of crystallization with seeding agent is described. Seed crystals are suspended in recycling concentrate flow. Owing to calcium carbonate depositing on the seeding agent the total salt content of concentrate decreases and high filtrate flow rate is provided that facilitates concentrate disposal. To implement the technology membrane apparatus with «open channel» are used that are resistant to the impact of membrane transfer of slightly water-soluble salts and suspended matter. Seed crystal growing is provided by dosing into concentrated caustic soda solution. Grown seed crystals were partially removed by sedimentation after hydraulic membrane wash. With the help of experimental diagrams it is possible to determine calcium carbonate crystallization rate depending on the influent water composition, the number of the seeded crystals, and filtrate yield. Process flow diagram of a continuously operating reverse osmosis plant is suggested. The methods of the process design are described: selecting the amount of recycling seed crystals, determining caustic soda consumption and tank size for calcium carbonate sludge precipitation. The estimations showed that to provide for calcium carbonate crystallization during continuous operation of the reverse osmosis plant caustic soda solution in amount of less than 5% of its stoichiometric amount required for the precipitation of the same amount of calcium carbonate from the influent water shall be regularly dosed into the recycling concentrate flow.

Key words: water stabilization, reverse osmosis plant, concentrate, calcium carbonate crystallization, seed crystals, concentrate utilization.

REFERENCES

- Apel'tsin I. E., Kliachko V. A. Opresnenie vody [Water desalination. Moscow, Stroiizdat Publ., 1968, 224 p.].

- Harries R. C. A field trial of seeded reverse osmosis for the desalination of a scaling-type mine water. Desalination, 1985, no. 56, pp. 227–236.

- Herrigel H. R. The seeded reverse osmosis process field testing: 12-th Annual Conference on Water Supply Improvement Association, Orlando. Florida, USA, May 13–18, 1984. Technology Proceedings, v. 1, sess. 1–6.

- Pervov A. G., Andrianov A. P., Iurchevskii E. B. [Improving the design of membrane apparatus]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2009, no. 7, pp. 62–68. (In Russian).

- Pervov A. G., Rudakova G. Ia., Efremov R. V. [Development of a program for technocal design of reverse osmosis and nanofiltration using Aminate chemicals]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2009, no. 7, pp. 21–29. (In Russian).

- Pervov A. G., Kozlova Iu. V., Andrianov A. P., Motovilova N. B. [Developing the technology of surface water purification with the use of nanofiltration membranes]. Kriticheskie Tekhnologii. Membrany, 2006, no. 1 (29), pp. 20–33. (In Russian).

- Pervov A. G., Andrianov A. P., Gorbunova T. P., Iurchevskii E. B. [The technology of reverse osmosis concentrate disposal in water treatment systems]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2012, no. 8, pp. 20–26. (In Russian).

- Pervov A. G., Efremov R. V., Spitsov D. V., Andrianov A. P., Gorbunova T. P. [Membrane methods in drinking water supply: membrane selection, water quality prediction, concentrate utilization]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2013, no. 6, pp. 15–21. (In Russian).

УДК 628.16.066.7

Вольфтруб Л. И. Опыт работы тонкослойных отстойников и осветлителей со встроенными камерами хлопьеобразования 41

Л. И. ВОЛЬФТРУБ*

* Вольфтруб Лия Иосифовна, кандидат технических наук, главный технолог, Группа компаний «ЭКОХОЛДИНГ»

125371, Россия, Москва, Волоколамское шоссе, 87, тел.: (495) 491-13-81, e-mail: volftrub@yandex.ru

Представлены результаты модернизации сооружений первой ступени обработки воды – камер хлопьеобразования, отстойников и осветлителей, основанных на использовании разработанных специалистами Группы компаний «ЭКОХОЛДИНГ» низкоскоростных и низконапорных рециркуляторов, а также тонкослойных сотоблоков, изготавливаемых из полиэтиленовой пленки толщиной 250–300 мкм. Разработанный метод соединения пленки в сотовую конструкцию, в процессе которого создается внутренний жесткий каркас, обеспечивает прочность и пространственную устойчивость сотоблока, а также позволяет растягивать его на рамах только по периметру. Прочное соединение пленки позволяет изготавливать сотовую конструкцию любого размера и угла наклона, что обеспечивает минимальные потери отстойной площади сооружений различной конфигурации – как круглых, так и прямоугольных. Для сооружений, находящихся в длительной эксплуатации, сотоблоки изготавливаются индивидуально после промеров каждого из них. Существенным преимуществом разработанных методов расчета и конструирования рециркуляторов является их возможность обеспечивать требуемую степень рециркуляции при небольших потерях напора и минимальных скоростях потока жидкости, что сохраняет рециркулируемую взвесь от разрушения и способствует эффективному хлопьеобразованию. Указанные высокоэффективные способы модернизации процессов хлопьеобразования и осаждения заложены в конструкциях блочных водоочистных установок заводского изготовления «Струя» и «Влага» производительностью 100–12000 м3/сут. Установки предназначены для очистки природных вод: снижения мутности и цветности, умягчения, обесфторивания, обезжелезивания (сложные формы, высокие концентрации железа) и обеззараживания. Они используются в системах водоснабжения поселков, небольших городов, больнично-санаторных комплексов, спортивных баз, рыбных хозяйств, промышленных предприятий или отдельных цехов.

Ключевые слова: водоподготовка, мутность, остаточный алюминий, осветлитель, тонкослойный отстойник, модернизация, сотоблок, камера хлопьеобразования.

Vol'ftrub L. I. The experience of operating lamella settlers and clarifiers with built-in flocculation chambers 41

L. I. VOL'FTRUB*

* Vol'ftrub Liia Iosifovna, PhD (Engineering), Chief Process Engineer, ECOHOLDING Group

87 Volokolamskoe Hwy., 125371 Moscow, Russian Federation, tel.: +7 (495) 491-13-81, e-mail: volftrub@yandex.ru

The results of upgrading primary water treatment facilities – flocculation chambers, sedimentation tanks and clarifiers based on the use of low-flow and low-pressure recirculators and lamella honeycomb modules made of polyethylene film 250–300 µm thick designed by ECOHOLDING Group experts are presented. The developed method of jointing film into a honeycomb construction with an inner rigid frame provides for the ruggedness and spacial stability of the honeycomb module and allows stretching it on the frames on perimeter only. Firm jointing of the film allows manufacturing a honeycomb construction of any size and angle of slope providing minimum loss of clarifying surface of the facilities of any configuration, both radial and rectangular. For long-term operated facilities honeycomb modules are tailormade after each of them has been measured. The possibility of ensuring the required recirculation rate at low head loss and minimum liquid flow rate to prevent the recycled suspension from destruction and facilitate efficient floc formation is an essential advantage of the developed methods of recirculator designing and constructing. The presented high-efficient methods of coagulation and sedimentation improvement form the basis of prefabricated «Struiia» and «Vlaga» modular water treatment units with 100–12000 m3/day capacities. The units are designed for natural water treatment: turbidity and color removal, softening, defluorination, de-ironing (composite forms, high concentrations of iron) and disinfection. They are used in water supply systems of settlements, towns, hospital care and health resorts, sport centers, fish farms, industrial enterprises or separate production facilities.

Key words: water treatment, turbidity, residual aluminium, clarifier, lamella settler, upgrade, honeycomb module, flocculation chamber.

От обработки осадка до выработки энергии: комплексное решение компании ANDRITZ (Австрия) 47

From sludge treatment to energy generation: ANDRITZ comprehensive solution (Austria) 47

ОЧИСТКА СТОЧНЫХ ВОД

УДК 628.35:661.63

Козлов М. Н., Кевбрина М. В., Николаев Ю. А., Дорофеев А. Г., Грачев В. А., Казакова Е. А., Асеева В. Г., Жарков А. В. Однореакторная технология удаления азота из сточных вод 53

М. Н. КОЗЛОВ1, М. В. КЕВБРИНА2, Ю. А. НИКОЛАЕВ3, А. Г. ДОРОФЕЕВ4, В. А. ГРАЧЕВ5, Е. А. КАЗАКОВА6, В. Г. АСЕЕВА7, А. В. ЖАРКОВ8

1 Козлов Михаил Николаевич, кандидат технических наук, начальник Управления новой техники и технологий, ОАО «Мосводоканал»

105005, Россия, Москва, Плетешковский пер., 2, тел.: (499) 263-93-64, e-mail: kozlov@mosvodokanal.ru

2 Кевбрина Марина Владимировна, кандидат биологических наук, начальник отдела очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-49-90, e-mail: kevbrina_mv@mosvodokanal.ru

3 Николаев Юрий Александрович, доктор биологических наук, главный специалист, отдел очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-52-33, e-mail: nikolaev_ya@mosvodokanal.ru

4 Дорофеев Александр Геннадьевич, кандидат биологических наук, главный специалист, отдел очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-52-33, e-mail: dorofeev_ag@mosvodokanal.ru

5 Грачев Владимир Анатольевич, кандидат сельскохозяйственных наук, ведущий инженер, отделение очистки сточных вод и обработки осадка, Курьяновские очистные сооружения, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-52-33, е-mail: grachev55@list.ru

6 Казакова Елена Александровна, кандидат технических наук, начальник технологического отдела, Производственное управление ВКХ Троицкого и Новомосковского административных округов, ОАО «Мосводоканал»

119297, Россия, Москва, Родниковая ул., 7, тел.: (495) 592-01-76, e-mail: kazakova_ea@mosvodokanal.ru

7 Асеева Вера Георгиевна, кандидат биологических наук, ведущий инженер, Управление новой техники и технологий, ОАО «Мосводоканал»

105005, Россия, Москва, Плетешковский пер., 2, тел.: (499) 263-03-29, e-mail: aseeva_vg@mosvodokanal.ru

8 Жарков Алексей Вячеславович, инженер, отделение очистки сточных вод и обработки осадка, Курьяновские очистные сооружения, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-16-13, е-mail: zharkov_mvk@mail.ru

В Инженерно-технологическом центре ОАО «Мосводоканал» разработана высокоэффективная технология удаления азота из сточных вод. Технология апробирована на Курьяновских очистных сооружениях г. Москвы для очистки фильтрата ленточных сгустителей сброженного осадка. Метод основан на использовании специфических Анаммокс-бактерий, окисляющих аммоний нитритом в бескислородных условиях. Очистка фильтрата протекает в реакторе периодического действия с полным перемешиванием (SBR-реактор). Процессы частичной нитрификации (окисление аммония до нитрита), окисление аммония нитритом и окисление органического вещества происходят в одном реакторе. Для всех реакторов существенной проблемой является удержание биомассы чрезвычайно медленно растущих бактерий Анаммокс. В рассматриваемом случае проблема решалась путем адгезии бактерий на стенках реактора и загрузочном материале, а также флотацией. Для определения показателей очистки использовали стандартные методы. Разработанная однореакторная модификация технологии аноксидного окисления аммония отличается от ранее известных по следующим параметрам: высокая эффективность удаления азота, способ удержания биомассы в реакторе, наличие новых бактерий Анаммокс, гетеротрофная денитрификация. При прочих равных условиях реализация однореакторной технологии Анаммокс требует десятикратно меньших объемов сооружений, чем двухреакторной, поэтому она предпочтительнее для внедрения. Новая технология получила название AUTOHETAMMOX.

Ключевые слова: сточные воды, удаление азота, нитри-денитрификация, Анаммокс-бактерии, биореактор.

СПИСОК ЛИТЕРАТУРЫ

- Kuba T., Van Loosdrecht M. C. M., Heijnen J. J. Phosphorus and nitrogen removal with minimal COD requirement by integration of denitrifying dephosphatation and nitrification in a two-sludge system // Water Research. 1996. V. 30. № 7. Р. 1702–1710.

- Jetten M. S. M., Strous M., Van de Pas-Schoonen K. T., Schalk J., Van Dongen U. G. J. M., Van de Graaf A. A., Logemann S., Muyzer G., Van Loosdrecht M. C. M., Kuenen J. G. The anaerobic oxidation of ammonium // FEMS Microbiology Reviews. 1999. V. 22. P. 421–437.

- Van Hulle S. W. H., Vandeweyer H. J. P., Meesschaert B. D., Vanrolleghem P. A., Dejans P., Dumoulin A. Engineering aspects and practical application of autotrophic nitrogen removal from nitrogen rich streams // Chemical Engineering Journal. 2010. V. 162. P. 1–20.

- Schmid M., Walsh K., Webb R., Rijpstra W. I. C., Van de Pas-Schoonen K., Verbruggen M. J., Hill T., Moffett B., Fuerst J., Schouten S., Sinninghe-Damsté J. S., Harris J., Shaw P., Jetten M., Strous M. Candidatus «Scalindua brodae», sp. nov., Candidatus «Scalindua wagneri», sp. nov., Two new species of anaerobic ammonium oxidizing bacteria // Systematic and Applied Microbiology. 2003. V. 26. P. 529–538.

- Храменков С. В., Козлов М. Н., Кевбрина М. В., Дорофеев А. Г., Казакова Е. А., Грачев В. А., Кузнецов Б. Б., Поляков Д. Ю., Николаев Ю. А. Новая бактерия, осуществляющая анаэробное окисление аммония в реакторе биологической очистки фильтрата сброженного осадка сточных вод // Микробиология. 2013. Т. 82. № 5. С. 625–634.

- http://www.mi-wea.org (дата обращения 28 марта 2014 г.).

- Szatkowska B., Cema G., Plaza E, Trela J., Hultman B. A one-stage system with partial nitritation and anammox processes in the moving-bed biofilm reactor // Water Science and Technology. 2007. V. 55. № 8–9. Р. 19–26.

- Dutch start-up first Anammox reactor // World Water and Environmental Engineering. 2006. March–April. 30 p.

- Wyffels S., Boeckx P., Pynaert K., Zhang D., Van Cleemput O., Chen G., Verstraete W. Nitrogen removal from sludge reject water by a two-stage oxygen-limited autotrophic nitrification denitrification process // Water Science and Technology. 2004. V. 49. № 5–6. Р. 57–64.

- Wett B. Solved up-scaling problems for implementing deammonification of rejection water // Water Science and Technology. 2006. V. 53. № 12. P. 121–128.

- EPA 832-R-12-011. Emerging technologies for wastewater treatment and in-plant wet weather management. March 2013.

- Improved control and application of nitrogen cycle bacteria for ammonia removal / Water technologies: results and opportunities: Research Directorate General. – Belgium, 2004. P. 8–12.

- Kalyuzhnyi S., Gladchenko M., Mulder A., Versprille B. DEAMOX – new biological nitrogen removal process based on anaerobic ammonia oxidation coupled to sulphide driven conversion of nitrate into nitrite // Water Research. 2006. V. 40. № 19. P. 3637–3645.

- Данилович Д. А., Козлов М. Н., Мойжес О. В., Николаев Ю. А., Казакова Е. А. Анаэробное окисление аммония для удаления азота из высококонцентрированных сточных вод // Водоснабжение и санитарная техника. 2010. № 4. С. 49–54.

- Vlaeminck S. E., De Clippeleir H., Verstraete W. Microbial resource management of one-stage partial nitritation/Anammox // Microbial Biotechnology. 2012. V. 5. № 3. Р. 433–448.

- Методика технологического контроля работы очистных сооружений городской канализации. – М.: Стройиздат, 1977. 304 с.

- Пат. 2492148, РФ. МПК C 02 F 3/34, C 02 F 3/30. Способ окисления аммония и труднодоступного органического вещества сточных вод в аэробно-аноксидных условиях (варианты) / Храменков С. В., Пахомов А. Н., Козлов М. Н., Николаев Ю. А., Дорофеев А. Г., Казакова Е. А. // Изобретения. Полезные модели. 2013. № 25.

- http://www.paques.nl/anammox (дата обращения 28 марта 2014 г.).

WASTEWATER TREATMENT

Kozlov M. N., Kevbrina M. V., Nikolaev Iu. A., Dorofeev A. G., Grachev V. A., Kazakova E. A., Aseeva V. G., Zharkov A. V. Single-reactor technology of nitrogen removal from wastewater 53

M. N. KOZLOV1, M. V. KEVBRINA2, Iu. A. NIKOLAEV3, A. G. DOROFEEV4, V. A. GRACHEV5, E. A. KAZAKOVA6, V. G. ASEEVA7, A. V. ZHARKOV8

1 Kozlov Mikhail Nikolaevich, PhD (Engineering), Head of Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

2 Pleteshkovskii lane, 105005 Moscow, Russian Federation, tel.: +7 (499) 263-93-64, e-mail: kozlov@mosvodokanal.ru

2 Kevbrina Marina Vladimirovna, PhD (Biology), Chief of Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-49-90, e-mail: kevbrina_mv@mosvodokanal.ru

3 Nikolaev Iurii Aleksandrovich, Doctor of Biology, Chief Specialist, Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-52-33, e-mail: nikolaev_ya@mosvodokanal.ru

4 Dorofeev Aleksandr Gennad'evich, PhD (Biology), Chief Specialist, Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-52-33, e-mail: dorofeev_ag@mosvodokanal.ru

5 Grachev Vladimir Anatol'evich, PhD (Agriculture), Leading Engineer, Wastewater and Sludge Treatment Department, Kur'ianovo Wastewater Treatment Plant, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-52-33, е-mail: grachev55@list.ru

6 Kazakova Elena Aleksandrovna, PhD (Engineering), Chief of Technological Department, Water and Wastewater Management Department, Troitzk and Novomoskovsk Administrative Districts, «Mosvodokanal» OJSC

7 Rodnikovaia str., 119297 Moscow, Russian Federation, tel.: (495) 592-01-76, e-mail: kazakova_ea@mosvodokanal.ru

7 Aseeva Vera Georgievna, PhD (Biology), Leading Engineer, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

2 Pleteshkovskii lane, 105005 Moscow, Russian Federation, tel.: +7 (499) 263-03-29, e-mail: aseeva_vg@mosvodokanal.ru

8 Zharkov Aleksei Viacheslavovich, Engineer, Wastewater and Sludge Treatment Department, Kur'ianovo Wastewater Treatment Plant, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-16-13, е-mail: zharkov_mvk@mail.ru

The experts of R&D Centre of «Mosvodokanal» OJSC developed high-effective technology of removing nitrogen from wastewater. The technology was tested at the Kur'ianovo wastewater treatment plant of the city of Moscow during processing filtrate of the digested sludge belt thickeners. The method is based on the use of specific Anammox-bacteria that oxidize ammonium with nitrite under anoxic conditions. Filtrate is processed in a sequencing batch reactor with complete mixing (SBR-reactor). Partial nitrification processes (ammonium oxidation into nitrite), ammonium oxidation with nitrite and organic matter oxidation are carried out in one reactor. Retention of extremely slow growing biomass of Anammox-bacteria has been a critical problem for all the reactors. In this particular case the problem was solved with bacteria adhesion on the reactor walls and the feed as well as with flotation. To evaluate the treatment efficiency standard methods were used. The developed single-reactor modification of the anoxic oxidation of ammonium differs from the well-known by the following parameters: high nitrogen removal efficiency, the method of biomass bacteria retention in the reactor, the availability of new Anammox bacteria, heterotrophic denitrification. All other conditions being equal the integration of Anammox single-reactor technology requires the size of the facilities ten times smaller than double-reactor technology; for this reason it is more preferable for implementation. The new technology was given the name AUTOHETAMMOX.

Key words: wastewater, nitrogen removal, nitrification-denitrification, Anammox-bacteria, bioreactor.

REFERENCES

- Kuba T., Van Loosdrecht M. C. M., Heijnen J. J. Phosphorus and nitrogen removal with minimal COD requirement by integration of denitrifying dephosphatation and nitrification in a two-sludge system. Water Research, 1996, v. 30, no. 7, pp. 1702–1710.

- Jetten M. S. M., Strous M., Van de Pas-Schoonen K. T., Schalk J., Van Dongen U. G. J. M., Van de Graaf A. A., Logemann S., Muyzer G., Van Loosdrecht M. C. M., Kuenen J. G. The anaerobic oxidation of ammonium. FEMS Microbiology Reviews, 1999, v. 22, pp. 421–437.

- Van Hulle S. W. H., Vandeweyer H. J. P., Meesschaert B. D., Vanrolleghem P. A., Dejans P., Dumoulin A. Engineering aspects and practical application of autotrophic nitrogen removal from nitrogen rich streams. Chemical Engineering Journal, 2010, v. 162, pp. 1–20.

- Schmid M., Walsh K., Webb R., Rijpstra W. I. C., Van de Pas-Schoonen K., Verbruggen M. J., Hill T., Moffett B., Fuerst J., Schouten S., Sinninghe Damsté J. S., Harris J., Shaw P., Jetten M., Strous M. Candidatus «Scalindua brodae», sp. nov., Candidatus «Scalindua wagneri», sp. nov., Two new species of anaerobic ammonium oxidizing bacteria. Systematic and Applied Microbiology, 2003, v. 26, pp. 529–538.

- Khramenkov S. V., Kozlov M. N., Kevbrina M. V., Dorofeev A. G., Kazakova E. A., Grachev V. A., Kuznetsov B. B., Poliakov D. Iu., Nikolaev Iu. A. [A new bacteria providing for anaerobic oxidation of ammonium in a biological reactor processing wastewater digested sludge filtrate]. Mikrobiologiia, 2013, v. 82, no. 5, pp. 625–634. (In Russian).

- http://www.mi-wea.org (accessed March 28, 2014).

- Szatkowska B., Cema G., Plaza E, Trela J., Hultman B. A one-stage system with partial nitritation and anammox processes in the moving-bed biofilm reactor. Water Science and Technology, 2007, v. 55, no. 8–9, pp. 19–26.

- Dutch start-up first Anammox reactor. World Water and Environmental Engineering, 2006, March–April, 30 p.

- Wyffels S., Boeckx P., Pynaert K., Zhang D., Van Cleemput O., Chen G., Verstraete W. Nitrogen removal from sludge reject water by a two-stage oxygen-limited autotrophic nitrification denitrification process. Water Science and Technology, 2004, v. 49, no. 5–6, pp. 57–64.

- Wett B. Solved up-scaling problems for implementing deammonification of rejection water. Water Science and Technology, 2006, v. 53, no. 12, pp. 121–128.

- EPA 832-R-12-011. Emerging technologies for wastewater treatment and in-plant wet weather management. March 2013.

- Improved control and application of nitrogen cycle bacteria for ammonia removal. Water technologies: results and opportunities: Research Directorate General. Belgium, 2004, pp. 8–12.

- Kalyuzhnyi S., Gladchenko M., Mulder A., Versprille B. DEAMOX – new biological nitrogen removal process based on anaerobic ammonia oxidation coupled to sulphide driven conversion of nitrate into nitrite. Water Research, 2006, v. 40, no. 19, pp. 3637–3645.

- Danilovich D. A., Kozlov M. N., Moizhes O. V., Nikolaev Iu. A., Kazakova E. A. [Anaerobic oxidation of ammonium for removal of nitrogen from high-concentrated wastewater]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2010, no. 4, pp. 49–54. (In Russian).

- Vlaeminck S. E., De Clippeleir H., Verstraete W. Microbial resource management of one-stage partial nitritation/Anammox. Microbial Biotechnology, 2012, v. 5, no. 3, pp. 433–448.

- Metodika tekhnologicheskogo kontrolia raboty ochistnykh sooruzhenii gorodskoi kanalizatsii [The technique of process monitoring of municipal wastewater treatment facilities. Moscow, Stroiizdat Publ., 1977, 304 p.].

- Khramenkov S. V., Pakhomov A. N., Kozlov M. N., Nikolaev Iu. A., Dorofeev A. G., Kazakova E. A. [Pat. 2492148, RF. IPC C 02 F 3/34, C 02 F 3/30. Method of oxidation of ammonium and problematic organics in wastewater under aerobic-anoxic conditions (options)]. Izobreteniia. Poleznye Modeli, 2013, no. 25.

- http://www.paques.nl/anammox (accessed March 28, 2014).

УДК 628.356

Дорофеев А. Г., Козлов М. Н., Асеева В. Г., Кевбрина М. В. Причины развития и методы контроля пенообразования в аэротенках 63

А. Г. ДОРОФЕЕВ1, М. Н. КОЗЛОВ2, В. Г. АСЕЕВА3, М. В. КЕВБРИНА4

1 Дорофеев Александр Геннадьевич, кандидат биологических наук, главный специалист, отдел очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-52-33, e-mail: dorofeev_ag@mosvodokanal.ru

2 Козлов Михаил Николаевич, кандидат технических наук, начальник Управления новой техники и технологий, ОАО «Мосводоканал»

105005, Россия, Москва, Плетешковский пер., 2, тел.: (499) 263-93-64, e-mail: kozlov@mosvodokanal.ru

3 Асеева Вера Георгиевна, кандидат биологических наук, ведущий инженер, Управление новой техники и технологий, ОАО «Мосводоканал»

105005, Россия, Москва, Плетешковский пер., 2, тел.: (499) 263-03-29, e-mail: aseeva_vg@mosvodokanal.ru

4 Кевбрина Марина Владимировна, кандидат биологических наук, начальник отдела очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-49-90, e-mail: kevbrina_mv@mosvodokanal.ru

На сооружениях биологической очистки сточных вод широко распространены явления пенообразования, вызванного развитием нитчатых форм микроорганизмов. Описаны типы пены, микроорганизмы, ответственные за вспухание и вспенивание активного ила. Проанализированы причины, способствующие массовому развитию нитчатых микроорганизмов в аэротенках: высокое содержание в сточной воде жиров или нефтепродуктов, высокий возраст ила и низкая концентрация растворенного кислорода в аэробных зонах аэротенков. Специалистами Инженерно-технологического центра ОАО «Мосводоканал» разработаны критерии оценки численности нитчатых нокардиоформных актиномицетов при микроскопировании образца. Приведен простой и практичный метод количественного учета нитчатых микроорганизмов активного ила, разработанный и используемый в ОАО «Мосводоканал». Особое внимание уделено используемым в мировой практике способам предотвращения и ликвидации пенообразования в аэротенках: улучшение работы первичных отстойников, регулирование возраста ила, оптимизация концентрации растворенного кислорода, хлорирование, использование селекторов, поверхностных ловушек для пены, пеногасителей, коагулянтов и полимеров. Анализ мировой практики свидетельствует о том, что меры для решения проблемы пенообразования должны подбираться с учетом особенностей используемой технологии и свойств поступающей сточной воды. Наиболее эффективными оказываются комплексные меры, охватывающие как краткосрочные, так и долговременные способы борьбы с пеной. В связи с тотальной распространенностью явления пенообразования на сооружениях биологической очистки муниципальных сточных вод представляется необходимым учитывать технические и технологические средства борьбы с пеной уже на стадии проектирования очистных сооружений.

Ключевые слова: сточные воды, биологическая очистка, пенообразование, нитчатые бактерии, вспухание активного ила, пеногаситель.

СПИСОК ЛИТЕРАТУРЫ

- Los Reyes F. L., Raskin L. Role of filamentous microorganisms in activated sludge foaming: relationship of mycolata levels to foaming initiation and stability // Water Research. 2002. V. 36. № 2. P. 445–59.

- Jenkins D., Richard M. G., Daigger G. T. Manual on the causes and control of activated sludge bulking and foaming: Water Research Commission. – Pretoria, South Africa, 1984.

- Eikelboom D. H. The Microthrix parvicella puzzle // Water Science and Technology. 1994. V. 29. № 7. P. 271–279.

- Richard M. Activated sludge microbiology problems and their control: National Operator Trainers Conference. – Buffalo, NY, June 8, 2003.

- Eikelboom D. H. Process control of activated sludge plants by microscopic investigation. – London: IWA Publishing, 2000.

- Jenkins D., Richard M. G., Daigger G. T. Manual on the causes and control of activated sludge bulking, foaming, and other solids separation problems. – Boca Raton: Lewis Publishers, 2004.

- Козлов М. Н., Дорофеев А. Г., Асеева В. Г. Микробиологический контроль активного ила биореакторов очистки сточных вод от биогенных элементов. – М.: Наука, 2012. 80 с.

- The causes and control of activated sludge bulking and foaming: summary report. –Washington, D.C.: U.S. EPA, 1987.

- Activated sludge separation problems theory, control measures, practical experiences. Editor(s): Tandoi V., Jenkins D., Wanner J. – IWA, 2006. 216 p.

- Kragelund C., Nilsson B., Eskilsson K., Fritzson K., Bogh A.-M., Nielsen P. H. Control of filamentous foam formers by chemical addition: Proceeding of the 12th Gothenburg symposium. – Ljubljana, Slovenia, May 20–23, 2007. P. 83–91.

- Paris S., Lind G., Lemmer H., Wilderer P. A. Dosing aluminum chloride to control Microthrix parvicella // Acta hydrochimica et hydrobiologica. 2005. V. 33. № 3. P. 247–254.

Dorofeev A. G., Kozlov M. N., Aseeva V. G., Kevbrina M. V. Causes and methods of control of foam formation in aeration tanks 63

A. G. DOROFEEV1, M. N. KOZLOV2, V. G. ASEEVA3, M. V. KEVBRINA4

1 Dorofeev Aleksandr Gennad'evich, PhD (Biology), Chief Specialist, Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kur'ianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-52-33, e-mail: dorofeev_ag@mosvodokanal.ru

2 Kozlov Mikhail Nikolaevich, PhD (Engineering), Head of Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

2 Pleteshkovskii lane, 105005 Moscow, Russian Federation, tel.: +7 (499) 263-93-64, e-mail: kozlov@mosvodokanal.ru

3 Aseeva Vera Georgievna, PhD (Biology), Leading Engineer, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

2 Pleteshkovskii lane, 105005 Moscow, Russian Federation, tel.: +7 (499) 263-03-29, e-mail: aseeva_vg@mosvodokanal.ru

4 Kevbrina Marina Vladimirovna, PhD (Biology), Chief of Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kur'ianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-49-90, e-mail: kevbrina_mv@mosvodokanal.ru

The phenomenon of foam formation caused by the development of filamentous microorganisms is a common problem observed at the wastewater treatment facilities. Foam types, microorganisms responsible for activated sludge bulking and foaming are described. The causes stimulating mass growth of filamentous microorganisms in aeration tanks: high concentration of grease and oil products in wastewater, high sludge age and low concentration of dissolved oxygen in aerobic zones of aeration tanks have been analyzed. The experts of R&D Centre of «Mosvodokanal» OJSC developed the criteria of evaluating the number of filamentous nocardioformic actinomycetes in the process of microscopic investigation of the sample. The simple and practical method of quantitative determination of activated sludge filamentous microorganisms developed and used in «Mosvodokanal» OJSC is presented. Special attention is paid to the methods used in the world practice for prevention and elimination of foaming in aeration tanks: improvement of primary settling tanks operation, sludge age control, optimization of dissolved oxygen concentration, chlorination, the use of extractors, surface foam traps, anti-foaming agents, coagulants and polymers. The analysis of world practice gives evidences that methods of foam control shall be selected with account of the specific features of the technology used and parameters of incoming wastewater. Comprehensive measures including both short-term and long-term methods of foam control turn to be most efficient. In connection with global prevalence of foaming phenomenon at the biological municipal wastewater treatment facilities it seems appropriate to take into account the technical and technological means of foam elimination already at the stage of designing treatment facilities.

Key words: wastewater, biological treatment, foaming, filamentous bacteria, activated sludge bulking, anti-foaming agent.

REFERENCES

- Los Reyes F. L., Raskin L. Role of filamentous microorganisms in activated sludge foaming: relationship of mycolata levels to foaming initiation and stability. Water Research, 2002, v. 36, no. 2, pp. 445–59.

- Jenkins D., Richard M. G., Daigger G. T. Manual on the causes and control of activated sludge bulking and foaming: Water Research Commission. Pretoria, South Africa, 1984.

- Eikelboom D. H. The Microthrix parvicella puzzle. Water Science and Technology, 1994, v. 29, no. 7, pp. 271–279.

- Richard M. Activated sludge microbiology problems and their control: National Operator Trainers Conference, Buffalo, NY, June 8, 2003.

- Eikelboom D. H. Process control of activated sludge plants by microscopic investigation. London, IWA Publishing, 2000.

- Jenkins D., Richard M. G., Daigger G. T. Manual on the causes and control of activated sludge bulking, foaming, and other solids separation problems. Boca Raton, Lewis Publishers, 2004.

- Kozlov M. N., Dorofeev A. G., Aseeva V. G. Mikrobiologicheskii kontrol' aktivnogo ila bioreaktorov ochistki stochnykh vod ot biogennykh elementov [Microbiological control of activated sludge in bioreactors removing nutrients from wastewater. Moscow, Nauka Publ., 2012, 80 p.].

- The causes and control of activated sludge bulking and foaming: summary report. Washington, D.C.: U.S. EPA, 1987.

- Activated sludge separation problems theory, control measures, practical experiences. Editor(s): Tandoi V., Jenkins D., Wanner J. IWA, 2006, 216 p.

- Kragelund C., Nilsson B., Eskilsson K., Fritzson K., Bogh A.-M., Nielsen P. H. Control of filamentous foam formers by chemical addition: Proceeding of the 12th Gothenburg symposium, Ljubljana, Slovenia, May 20–23, 2007, pp. 83–91.

- Paris S., Lind G., Lemmer H., Wilderer P. A. Dosing aluminum chloride to control Microthrix parvicella. Acta hydrochimica et hydrobiologica, 2005, v. 33, no. 3, pp. 247–254.

УДК 628.35:661.5

Кевбрина М. В., Гаврилин А. М., Козлов И. М. Новая организация процесса преферментации для удаления биогенных элементов из сточных вод 73

М. В. КЕВБРИНА1, А. М. ГАВРИЛИН2, И. М. КОЗЛОВ3

1 Кевбрина Марина Владимировна, кандидат биологических наук, начальник отдела очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-49-90, e-mail: kevbrina_mv@mosvodokanal.ru

2 Гаврилин Александр Михайлович, начальник Инженерно-технологического центра, Управление новой техники и технологий, ОАО «Мосводоканал»

105005, Россия, Москва, Плетешковский пер., 2, тел.: (499) 763-34-34, e-mail: gavrilin_am@mosvodokanal.ru

3 Козлов Иван Михайлович, инженер, отдел очистки сточных вод, Инженерно-технологический центр, Управление новой техники и технологий, ОАО «Мосводоканал»

109235, Россия, Москва, 1-й Курьяновский проезд, 15, тел.: (495) 348-16-13, е-mail: kozlov-ivan@mail.ru

Концентрация легкодоступного органического вещества определяет стабильность процесса биологического удаления фосфора из сточных вод. Для городских сточных вод Москвы характерно невысокое значение этого показателя. Одним из методов увеличения доли легкодоступной органики является преферментация (ацидофикация) сырого осадка сточных вод. На промышленных аэротенках московских очистных сооружений, работающих по технологической схеме Кейптаунского университета (UCT), реализована новая схема организации процесса преферментации. В отличие от классической схемы проведения преферментации, протекающей в первичном отстойнике или реакторе-преферментере, процесс организован в первой анаэробной зоне аэротенка. Там, при отсутствии перемешивания иловой смеси, происходит формирование уплотненного слоя активного ила, сопровождающееся преферментацией сорбированного на иле органического вещества. При этом анаэробная зона продолжает выполнять свою основную функцию в очистке сточной воды, связанную с биологическим высвобождением фосфатов за счет потребления летучих жирных кислот фосфатаккумулирующими бактериями. Увеличение содержания летучих жирных кислот в иловой смеси в анаэробной зоне аэротенка за счет преферментации способствует более стабильному удалению фосфатов из очищаемой воды. Организация процесса преферментации в первом коридоре аэротенка является более перспективной и экономически выгодной по сравнению с классической организацией процесса в отстойниках-преферментерах за счет экономии затрат на перемешивание и отсутствия необходимости строительства или реконструкции дополнительных емкостей (преферментеров, отстойников).

Ключевые слова: сточные воды, сырой осадок, биологическая дефосфатация, преферментация, ацидофикация, легкодоступное органическое вещество.

СПИСОК ЛИТЕРАТУРЫ

- Randall C. W., Barnard J. L., Stensel H. D. Design and retrofit of wastewater treatment plants for biological nutrient removal. – Lancaster, Pennsylvania, USA, Water Quality Management Library. Technomic Publishing Company, 1992. V. 5. P. 125–126.

- Reddy M. Biological and chemical systems for nutrient removal: special publication. – WEF, 1998. ISBN 1-57278-123-8.

- Münch E. DSP-prefermenter technology book. – Brisbane, Australia, Science Traveller International Advanced Wastewater Management Centre, 1998.

- Do P., Amatya P. L., Keller W. E. Successful implementation of biological nutrient removal at Calgary’s 500 ml/d Bonnybrook wastewater treatment plant. Available at: http://library.queensu.ca/ojs/index.php/PCEEA/article/view/3893/3977 (дата обращения  18 апреля 2014 г.).

- http://www.waterandwastewater.com/plant_directory/Detailed/222.html (дата обращения 20 января 2014 г.).

- www.hobartcity.com.au (дата обращения 18 апреля 2014 г.).

- http://www.sydneywater.com.au/Education/pdf/3-6-3-3-7SMSTP.pdf (дата обращения 20 января 2014 г.).

- Беляев А. Н., Васильев Б. В., Маскалева С. Е., Мишуков Б. Г., Соловьева Е. А. Удаление азота и фосфора на канализационных очистных сооружениях // Водоснабжение и санитарная техника. 2008. № 9. C. 38–43.

- Стрелков А. К., Шувалов М. В., Астраханцев Д. В., Дударев В. А., Степанов С. В., Тараканов Д. И. Концепция реконструкции городских очистных сооружений канализации г. Самары // Водоснабжение и санитарная техника. 2011. № 9. С. 46–50.

- Колясева О. В., Кисляков А. А. В поселке Ува будут работать современнные канализационные очистные сооружения // Промышленная и экологическая безопасность. 2008. № 2.

- Кевбрина М. В., Гаврилин А. М., Белов Н. А., Газизова Н. Г., Асеева В. Г. Ацидификационный потенциал поступающей сточной воды и сырого осадка московских очистных сооружений // Водоснабжение и санитарная техника. 2012. № 10. С. 68–70.

- Козлов М. Н., Стрельцов С. А., Кевбрина М. В., Гаврилин А. М., Газизова Н. Г. Ацидофикация (преферментация) как метод стабилизации сырого осадка при очистке сточных вод от биогенных элементов // Водоснабжение и санитарная техника. 2013. № 5. С. 13–20.

- Пахомов А. Н., Стрельцов С. А., Козлов М. Н., Харькина О. В., Хамидов М. Г., Ершов Б. А., Белов Н. А. Опыт эксплуатации сооружений биологической очистки сточных вод от соединений азота и фосфора // Водоснабжение и санитарная техника. 2010. № 10. С. 35–41.

Kevbrina M. V., Gavrilin A. M., Kozlov I. M. The new form of pre-fermentation process arrangement for removing nutrients from wastewater 73

M. V. KEVBRINA1, A. M. GAVRILIN2, I. M. KOZLOV3

1 Kevbrina Marina Vladimirovna, PhD (Biology), Chief of Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-49-90, e-mail: kevbrina_mv@mosvodokanal.ru

2 Gavrilin Aleksandr Mikhailovich, Chief of R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

2 Pleteshkovskii lane, 105005 Moscow, Russian Federation, tel.: +7 (499) 763-34-34, e-mail: gavrilin_am@mosvodokanal.ru

3 Kozlov Ivan Mikhailovich, Engineer, Wastewater Treatment Section, R&D Centre, Advanced Equipment and Technologies Department, «Mosvodokanal» OJSC

15, 1st Kurianovskii proezd, 109235 Moscow, Russian Federation, tel.: +7 (495) 348-16-13, е-mail: kozlov-ivan@mail.ru

The concentration of readily available organic matter determines the process stability of biological phosphorus removal from wastewater. The low value of this parameter is typical for municipal wastewater in Moscow. Raw wastewater sludge pre-fermentation (acidofication) is one of the methods of increasing the readily available organic matter fraction. A new arrangement of pre-fermentation process has been implemented in the industrial-scale aeration tanks of the Moscow wastewater treatment facilities operating after the process flow scheme of the University of Cape Town (UCT). Compared to the traditional pre-fermentation process flow scheme taking place in a primary settling tank or reactor prefermenter the process is arranged in the first anaerobic zone of the aeration tank. Here, in the absence of mixed liquor mixing, a thickened layer of activated sludge is formed accompanied by pre-fermentation of organic matter sorbed onto sludge. Meanwhile the anaerobic zone carries on its main function in the treatment process related to biological phosphorus release by means of phosphate accumulating bacteria consuming volatile fatty acids. Increasing the concentration of volatile fatty acids in mixed liquor in anaerobic zone by means of pre-fermentation stabilizes phosphate removal from processed wastewater. Arranging pre-fermentation process in the first corridor of the aeration tank is more advanced and cost-effective compared to the traditional process arrangement in settlers-prefermenters owing to saving expenditures on mixing and eliminating construction or upgrade of additional tanks (prefermenters, settling tanks).

Key words: wastewater, raw sludge, biological dephosphatation, pre-fermentation, acidofication, readily available organic matter.

REFERENCES

- Randall C. W., Barnard J. L., Stensel H. D. Design and retrofit of wastewater treatment plants for biological nutrient removal. Lancaster, Pennsylvania, USA, Water Quality Management Library. Technomic Publishing Company, 1992, v. 5, pp. 125–126.

- Reddy M. Biological and chemical systems for nutrient removal: special publication. WEF, 1998. ISBN 1-57278-123-8.

- Münch E. DSP-prefermenter technology book. Brisbane, Australia, Science Traveller International Advanced Wastewater Management Centre, 1998.

- Do P., Amatya P. L., Keller W. E. Successful implementation of biological nutrient removal at Calgary’s 500 ml/d Bonnybrook wastewater treatment plant. Available at: http://library.queensu.ca/ojs/index.php/PCEEA/article/view/3893/3977 (accessed April 18, 2014).

- http://www.waterandwastewater.com/plant_directory/Detailed/222.html (accessed January 20, 2014).

- www.hobartcity.com.au (accessed April 18, 2014).

- http://www.sydneywater.com.au/Education/pdf/3-6-3-3-7SMSTP.pdf. (accessed January 20, 2014).

- Beliaev A. N., Vasil'ev B. V., Maskaleva S. E., Mishukov B. G., Solov'eva E. A. [Removal of nitrogen and phosphor at sewerage treatment facilities]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2008, no. 9, pp. 38–43. (In Russian).

- Strelkov A. K., Shuvalov M. V., Astrakhantsev D. V., Dudarev V. A., Stepanov S. V., Tarakanov D. I. [Conception of reconstruction of city sewerage treatment facilities of Samara]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2011, no. 9, pp. 46–50. (In Russian).

- Koliaseva O. V, Kisliakov A. A. [Advanced wastewater treatment facilities will be operating in Uva community]. Promyshlennaia i ekologicheskaia bezopasnost', 2008, no. 2. (In Russian).

- Kevbrina M. V., Gavrilin A. M., Belov N. A., Gazizova N. G., Aseeva V. G. [Acidification potential of the incoming wastewater and raw sludge at the Moscow wastewater treatment facilities]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2012, no. 10, pp. 68–70. (In Russian).

- Kozlov M. N., Strel'tsov S. A., Kevbrina M. V., Gavrilin A. M., Gazizova N. G. [Acidification (pre-fermentation) as a method of raw sludge stabilization in the process of nutrients removal from wastewater]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2013, no. 5, pp. 13–20. (In Russian).

- Pakhomov A. N., Strel'tsov S. A., Kozlov M. N., Khar'kina O. V., Khamidov M. G., Ershov B. A., Belov N. A. [Experience of operating the facilities for biological removal of nitrogen and phosphorus compounds from wastewater]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2010, no. 10, pp. 35–41. (In Russian).