ЗАКОНЫ, СТАНДАРТЫ, НОРМАТИВЫ

УДК 628.1.033:351.777

Самбурский Г. А., Плитман С. И., Пестов С. М., Тулакин А. В., Амплеева Г. П. О некоторых проблемах водоподготовки в части реализации закона «О водоснабжении и водоотведении» 4

Г. А. САМБУРСКИЙ1, С. И. ПЛИТМАН2, С. М. ПЕСТОВ3, А. В. ТУЛАКИН4, Г. П. АМПЛЕЕВА5

1 Самбурский Георгий Александрович, кандидат технических наук, доцент, руководитель департамента водоподготовки, Российская ассоциация водоснабжения и водоотведения

119334, Россия, Москва, Ленинский проспект, 38, корп. 2, тел.: (495) 939-19-36, e-mail: gesamb@yandex.ru

2 Плитман София Исааковна, доктор медицинских наук, профессор, НИИ медицины труда Российской академии медицинских наук

105275, Россия, Москва, проспект Буденного, 31, тел.: (495) 365-31-30, e-mail: koshenkov1937@mail.ru

3 Пестов Сергей Михайлович, доктор химических наук, доцент, Московский технологический университет

119454, Россия, Москва, проспект Вернадского, 78, тел.: (495) 246-05-55, e-mail: mitht@mitht.ru

4 Тулакин Андрей Васильевич, доктор медицинских наук, профессор, заместитель директора по научной работе, Федеральный научный центр гигиены имени Ф. Ф. Эрисмана Роспотребнадзора

141000, Россия, Московская область, г. Мытищи, ул. Семашко, 2, тел.: (495) 582-96-68, e-mail: voda@fferisman.ru

5 Амплеева Галина Петровна, кандидат медицинских наук, Федеральный научный центр гигиены имени Ф. Ф. Эрисмана Роспотребнадзора

141000, Россия, Московская область, г. Мытищи, ул. Семашко, 2, тел.: (495) 582-96-68, e-mail: voda@fferisman.ru

Рассмотрены некоторые проблемы регламентирования технологического процесса подготовки питьевой воды для централизованных систем водоснабжения в части соответствия качества воды установленным гигиеническим требованиям и целевым показателям деятельности. Показано, что при использовании методики оценки риска предприятия водопроводно-канализационного хозяйства имеют возможность оптимизировать мероприятия по улучшению качества питьевой воды с точки зрения выбора сроков реализации и приоритета. Отмечено, что измерение показателей качества воды без учета погрешностей метода и выборки может не отражать реальные значения концентрации загрязняющих веществ в питьевой воде централизованных систем водоснабжения, а превышение по ПДК может быть более чем пятикратным, что противоречит как требованиям гигиенического нормирования качества питьевой воды, так и критериям существенного ухудшения качества питьевой воды.

Ключевые слова: водоподготовка, питьевая вода, водоснабжение, риск для здоровья, качество воды, погрешность измерения.

СПИСОК ЛИТЕРАТУРЫ

  - Плитман С. И., Беспалько Л. Е., Тулакин А. В., Цыплакова Г. В., Амплеева Г. П. О гигиенической безопасности при внедрении закона «О водоснабжении и водоотведении» // Санитарный врач. 2014. № 3. С. 10–15.

  - Плитман С. И., Тулакин А. В., Амплеева Г. П. К вопросу о надежности гигиенических нормативов Единых требований Таможенного союза // Санитарный врач. 2014. № 11. С. 57–60.

LAWS, STANDARDS, NORMATIVES

Samburskii G. A., Plitman S. I., Pestov S. M., Tulakin A. V., Ampleeva G. P. On some problems in water treatment related to the implementation of «On water supply and wastewater disposal» Act 4

G. A. SAMBURSKII1, S. I. PLITMAN2, S. M. PESTOV3, A. V. TULAKIN4, G. P. AMPLEEVA5

1 Samburskii Georgii Aleksandrovich, Ph. D. (Engineering), Assistant Professor, Head of Water Treatment Department, Russian Water and Wastewater Association

Build. 2, 38 Leniskii ave., 119334, Moscow, Russian Federation, tel.: +7 (495) 939-19-36, e-mail: gesamb@yandex.ru

2 Plitman Sofiia Isaakovna, Doctor of Medical Science, Professor, Research Institute for Occupational Medicine, Russian Academy of Medical Sciences

31 Budennogo ave., 105275, Moscow, Russian Federation, tel.: +7 (495) 365-31-30, e-mail: koshenkov1937@mail.ru

3 Pestov Sergei Mikhailovich, Doctor of Chemistry, Assistant Professor, Moscow Technological University

78 Vernadskogo ave., 119454, Moscow, Russian Federation, tel.: +7 (495) 246-05-55, e-mail: mitht@mitht.ru

4 Tulakin Andrei Vasil'evich, Doctor of Medical Science, Professor, Deputy Director for Science, Federal Scientific Centre for Hygiene named after F. F. Erisman, Rospotrebnadzor

2 Semashko str., 141000, Mytishchi, Moscow Area, Russian Federation, tel.: +7 (495) 582-96-68, e-mail: voda@fferisman.ru

5 Ampleeva Galina Petrovna, Ph. D. (Medical Science), Federal Scientific Centre for Hygiene named after F. F. Erisman, Rospotrebnadzor

2 Semashko str., 141000, Mytishchi, Moscow Area, Russian Federation, tel.: +7 (495) 582-96-68, e-mail: voda@fferisman.ru

A number of problems of regulating the process of drinking water purification for public water supply systems related to the water quality meeting the established hygienic requirements and performance targets are considered. It is shown that water and wastewater providers using the methods of risk assessment can optimize the measures aimed at improving the quality of drinking water in the context of choosing the implementation dates and priorities. It is noted that measuring water quality parameters without any consideration for procedural and sampling errors may not reflect actual concentrations of pollutants in drinking water in public water supply systems; whereas five-fold exceeding maximum permissible concentrations is possible which contravenes both drinking water hygienic standards and criteria of significant drinking water quality deterioration.

Key words: water treatment, drinking water, water supply, health risk, water quality, measurement error.

REFERENCES

- Plitman S. I., Bespal'ko L. E., Tulakin A. V., Tsyplakova G. V., Ampleeva G. P. [On sanitary safety in the implementation of «On water supply and wastewater disposal» Act]. Sanitarnyi Vrach, 2014, no. 3, pp. 10–15. (In Russian).

- Plitman S. I., Tulakin A. V., Ampleeva G. P. [On the reliability of the hygienic regulations in the standard requirements of the Customs Union]. Sanitarnyi Vrach, 2014, no. 11, pp. 57–60. (In Russian).

ПИТЬЕВОЕ ВОДОСНАБЖЕНИЕ

УДК 628.16.081

Фомина В. Ф., Фомин А. В. Опыт эксплуатации напорных флотаторов при очистке маломутных цветных вод реки Вычегды 9

(к 10-летию ввода блока напорных флотаторов на ВОС г. Сыктывкара)

В. Ф. ФОМИНА1, А. В. ФОМИН2

1 Фомина Валентина Федоровна, кандидат технических наук, старший научный сотрудник, Институт социально-экономических и энергетических проблем Севера Коми Научного Центра Уральского отделения Российской академии наук

167982, Россия, г. Сыктывкар, Коммунистическая ул., 26, тел.: (8212) 24-53-56, е-mail: fomina@iespn.komisc.ru

2 Фомин Александр Васильевич, кандидат экономических наук, заместитель начальника планово-экономического отдела, ОАО «Сыктывкарский водоканал»

167001, Россия, г. Сыктывкар, Коммунистическая ул., 51а, тел.: (8212) 32-89-62, е-mail: eastsir@mail.ru

Приведены результаты эксплуатации блока напорных флотаторов производительностью 65 тыс. м3/сут, запущенных в работу в мае 2006 г. на очистных сооружениях водопровода г. Сыктывкара. В течение 10 лет блок флотаторов успешно функционирует, обеспечивая высокую степень осветления питьевой воды. Анализ основных показателей качества очищенной воды после каждой ступени очистных сооружений подтвердил, что для очистки маломутной цветной воды р. Вычегды метод напорной флотации является наиболее эффективным. Показано, что в отдельные периоды года при повышении цветности более 150–200 град и снижении температуры воды возникают сложности с обеспечением норматива по показателю перманганатной окисляемости и требуется более тщательный подбор реагентов и оптимизация их доз. При оптимальном режиме коагулирования метод напорной флотации обеспечивает глубокое осветление воды до значения мутности менее 1 мг/л, что позволяет рассматривать фильтры в качестве барьерных сооружений на случай «проскока» мутности.

Ключевые слова: маломутные цветные воды, напорная флотация, реагентная обработка, фильтрование, коагуляция, промывные воды.

СПИСОК ЛИТЕРАТУРЫ

- Кофман В. Я. Напорная флотация в водоподготовке (обзор зарубежных изданий) // Водоснабжение и санитарная техника. 2013. № 5. С. 44–48.

- Пат. 443844, СССР. МПК C 02 F 1/24, B 03 D 1/04, C 02 F 1/52. Способ очистки природной воды / Сийрде Э. К., Сутт И. И., Мунтер Р. Р., Лооритс Х. А. // Открытия. Изобретения. 1974. № 35.

- Демин И. И., Трескунов В. М. Осветление природных вод методом напорной флотации / Методы и средства улучшения качества питьевой воды и обработки осадков водопроводных станций: Научные труды АКХ им. К. Д. Памфилова. Вып. 141. – М., ОНТИ АКХ, 1977. С. 3–11.

- Демин И. И. Применение метода напорной флотации в технологии обработки воды для хозяйственно-питьевых целей: Дис. … канд. техн. наук. – М., 1977. 183 с.

- Фомина В. Ф., Фомин В. П. Эффективность очистки маломутной цветной воды в напорных флотаторах на ВОС г. Сыктывкара // Водоснабжение и санитарная техника. 2012. № 4. С. 37–43.

DRINKING WATER SUPPLY

Fomina V. F., Fomin A. V. The experience of operating pressure flotation facilities for the purification of low-turbid colored water of the Vychegda River 9

(on the occasion of 10 years of the startup of pressure flotation facilities at the water treatment plant of Syktyvkar)

V. F. FOMINA1, A. V. FOMIN2

1 Fomina Valentina Fedorovna, Ph. D. (Engineering), Senior Research Worker, Institute for Social, Economic and Energy Problems of Northern Komi, Scientific Centre of the Ural Division of the Russian Academy of Sciences

26 Kommunisticheskaia str., 167982, Syktyvkar, Russian Federation, tel.: +7 (8212) 24-53-56, е-mail: fomina@iespn.komisc.ru

2 Fomin Aleksandr Vasil'evich, Ph. D. (Economics), Deputy Chief of Panning-and-Economic Department, «Syktyvkarskii Vodokanal» OJSC

51a Kommunisticheskaia str., 167001, Syktyvkar, Russian Federation, tel.: +7 (8212) 32-89-62, е-mail: eastsir@mail.ru

The results of operating the pressure flotation facilities with a capacity of 65,000 m3/day commissioned in May 2006 at the water treatment plant of Syktyvkar are considered. During 10 years the pressure flotation facilities have been successfully operating and ensuring high-level clarification of drinking water. The analysis of the main water quality indicators after each treatment stage showed that the pressure flotation method had been the most efficient for purification of low-turbid colored water of the Vychegda River. It is stated that during certain seasons color increase higher than 150–200 grades and temperature decrease result in complications with meeting the standard for permanganate oxidizability; therefore more detailed selection of chemical agents and dosage optimization is required. At the optimal coagulation operation mode the method of pressure flotation provides for enhanced water clarification to less than 1 mg/l turbidity which allows using filters as barrier facilities in case of turbidity breakthrough.

Key words: low-turbid colored water, pressure flotation, chemical treatment, filtration, coagulation, wash water.

REFERENCES

- Kofman V. Ia. [Pressure flotation in water treatment (review of foreign literature)]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2013, no. 5, pp. 44–48. (In Russian).

- Siirde E. K., Sutt I. I., Munter R. R., Loorits Kh. A. [Patent 443844, USSR. IPC C 02 F 1/24, B 03 D 1/04, C 02 F 1/52. Method of natural water treatment]. Otkrytiia. Izobreteniia, 1974, no. 35. (In Russian).

- Demin I. I., Treskunov V. M. [Natural water clarification by pressure flotation. Methods and means of improving drinking water and water sludge treatment]. Collection of research papers of Public Utilities Academy named after K. D. Pamfilov. Issue 141. Moscow, ONTI AKH Publ., 1977, pp. 3–11.

- Demin I. I. Primenenie metoda napornoi flotatsii v tekhnologii obrabotki vody dlia khoziaistvenno-pit'evykh tselei [The use of pressure flotation method in water treatment for public water supply: Ph. D. thesis in Engineering Science. Moscow, 1977, 183 p.].

- Fomina V. F., Fomin V. P. [Efficiency of low-turbid colored water purification in pressure flotators at the water treatment plant of Syktyvkar]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2012, no. 4, pp. 37–43. (In Russian).

УДК 628.16.067.1

Филатов А. И. О некоторых особенностях расчета дренажно-распределительных систем скорых фильтров большой площади 17

А. И. ФИЛАТОВ*

* Филатов Алексей Иванович, кандидат технических наук, заместитель генерального директора по науке, ОАО «Ростовский НИИКХ»

344000, Россия, г. Ростов-на-Дону, ул. Текучева, 207, тел.: (863) 251-55-92, e-mail: rniikh@gmail.com

Известны два основных способа расчета дренажно-распределительных систем для равномерной промывки скорых фильтров: по отношению суммарной площади отверстий дренажа к площади фильтра и по так называемому конструктивному отношению суммарной площади отверстий дренажа к площади поперечного сечения коллектора. Второй способ представляется более логичным, так как напрямую связывает значения восстанавливающихся скоростных напоров в трубах с необходимой общей величиной потери напора в дренаже, требующейся для равномерной промывки фильтра. При использовании этого способа расчета для фильтров большой площади предлагается учитывать падение напора при имеющемся резком расширении поперечного сечения потока промывной воды в начале центрального (бокового) канала.

Ключевые слова: скорый фильтр, дренажно-распределительная система, центральный канал, потери напора, равномерность промывки.

СПИСОК ЛИТЕРАТУРЫ

- Клячко В. А., Апельцин И. Э. Подготовка воды для промышленного и городского водоснабжения. – М.: Госстройиздат, 1962, 860 с.

- Абрамович Г. Н. Теория турбулентных струй. – М.: Физматгиз, 1960, 138 с.

- Чугаев Р. Р. Гидравлика. – М.: Энергия, 1970, 552 с.

Filatov A. I. On some specific features of calculating drainage-distribution systems of large area rapid filters 17

A. I. FILATOV*

* Filatov Aleksei Ivanovich, Ph. D. (Engineering), Deputy General Director for Science, «Rostovskii NIIKH» OJSC

207 Tekucheva str., 344000, Rostov-on-Don, Russian Federation, tel.: + 7 (863) 251-55-92, e-mail: rniikh@gmail.com

Two main methods of calculating drainage-distribution systems for uniform washing of rapid filters are known: as regards the relation of the total surface area of drainage slots to the filter area and as regards the so-called relation of the total surface area of drainage slots to the cross-sectional area of the collecting manifold. The second method seems to be more consistent since it provides for the direct link between the values of the recoverable dynamic pressure in the pipes and the total head loss in the drainage required for the uniform filter wash. When using this method for calculating large area filters it is suggested to take into consideration the head loss at the sudden expansion of the cross section of the wash water flow at the head of the central (side) canal.

Key words: rapid filter, drainage-distribution system, central canal, head losses, uniform washing.

REFERENCES

- Kliachko V. A., Apel'tsin I. E. Podgotovka vody dlia promyshlennogo i gorodskogo vodosnabzheniia [Water purification for industrial and public water supply. Moscow, Gosstroiizdat Publ., 1962, 860 p.].

- Abramovich G. N. Teoriia turbulentnykh strui [Theory of turbulent streams. Moscow, Fizmatgiz Publ., 1960, 138 p.].

- Chugaev R. R. Gidravlika [Hydraulics. Moscow, Energiia Publ., 1970, 552 p.].

Удк 628.179

Гальперин Е. М. Утечки воды в водопроводной сети 21

Е. М. ГАЛЬПЕРИН*

* Гальперин Евгений Моисеевич, кандидат технических наук, профессор кафедры «Водоснабжение и водоотведение», Самарский государственный архитектурно-строительный университет

443001, Россия, г. Самара, Молодогвардейская ул., 194, тел.: (846) 339-14-11, e-mail: evg-galperin@yandex.ru

Обеспечить герметичность водопроводной сети, имеющей сотни километров трубопроводов, находящихся под давлением и проложенных в земле, иногда в агрессивных грунтах и подземных водах, практически невозможно. Утечки из водопроводной сети являются непременным элементом ее эксплуатации. Потери воды питьевого качества при ее транспортировке приносят ощутимый экономический ущерб водоснабжающим организациям, способствуют повышению уровня подземных вод, в ряде случаев наносят вред окружающей среде. Персонал, эксплуатирующий водопроводные сети, ведет непрерывную работу по сокращению утечек воды. Борьба с утечками воды из водопроводной сети является частью работы по ее эксплуатации. Приводится информация о величине утечек и потерь воды в отдельных странах мира. Подробно представлен опыт предотвращения утечек в водопроводной сети г. Токио, в котором утечки – одни из самых низких в мире.

Ключевые слова: водопроводная сеть, утечки и потери воды, трубопровод, сейсмическая устойчивость, приборы диагностики.

СПИСОК ЛИТЕРАТУРЫ

- Методика определения неучтенных расходов и потерь воды в системах коммунального водоснабжения // ЖКХ: журнал руководителя и главного бухгалтера. 2006. № 1, 2. 51 с.

- Лернер А. Д. Неучтенные расходы в системах коммунального водоснабжения и водоотведения // Водоснабжение и санитарная техника. 2005. № 4. С. 9–12.

- Лернер А. Д., Домнин К. В., Бойко С. В., Кочетова М. Г. Проблемы обоснования величины неучтенных расходов воды в системах водоснабжения и водоотведения // Водоснабжение и санитарная техника. 2012. № 7. С. 64–70.

- Hiroki Ariyoshi. Strategy for water leakage control in Japan / JWA Workshop of Water & Energy and Water Loss, 2014. 14 p.

- Beuken R. H. S., Lavooij C. S. W., Bosch A., Schaap P. G. Low leakage in the Netherlands Confirmed: Proceedings of the 8th Annual Water Distribution Systems Analysis Symposium (ASCE). – USA, Cincinnati, 2006.

- Beecher J. A. Survey of State Agency Water Loss Reporting Practices. – AWWA, Colorado, USA, 2002. 10 p.

- OFWAT. Service and delivery-performance of the water companies in England and Wales 2009–10 report. QFWAT. UK, 2010.

- Fantozzi M. Italian case study in applying IWA WLTF approach: results obtained: Eds. J. Thornton, R. Sturm, G. Kunkel / Water Loss Control. – New York, McGraw-Hill, 2008. P. 421–432.

- Marques R. C., Monteiro A. J. Application of performance indicators to control loses- results from the Portuguese water sector // Water Science and Technology: Water Supply. 2003. № 3 (1,5). P. 127–133.

- Kanakoudis V., Tsitsifli S. Results of an urban water distribution network performance evaluation attempt in Greece // Urban Water Journal. 2010. № 7 (5). P. 267–285.

- Carpenter Т., Lambert A., McKenzie R. Applying the IWA approach to water loss performance indicators in Australia // Water Science and Technology: Water Supply. 2003. № 3 (1/2). Р. 153–161.

- Zechner F. Time for a change / The Undergrounder. Ontario Sewer and Watermain Construction Association, 2007. P. 9.

- ADB. Every Drop Counts: Learning from Good Practices in Eight Asian Cities. – Asian Development Bank, Manila, 2010.

- Cheung P. B., Girl G. V. Night now analysis and modeling for leakage estimation in a water distribution system / Integrating Water Systems: Eds. Boxall, Maksimovic. – Taylor and Francis Group, London, 2009.

- Babic B., Dukin A., Stanic M. Managing water pressure for water savings in developing countries. – Serbia, University of Belgrade, 2014. P. 122–132.

- Welcome to Bureau of Waterworks, Tokyo Metropolitan Government / For Water Professionals, 2013. https://www.waterprofessionals.metro.tokyo.jp/ (дата обращения 22.04.2016).

- Mutikanga H. E. Water loss management: Tool and for development countries: Dissertation of degree of doctor to be defended. The Netherlands, June 4, 2012.

- Prevention of Water Leakage in Tokyo. – Bureau of Waterworks, Tokyo Metropolitan Government, 2014.

- Leakage Prevention in Tokyo. – Bureau of Waterworks, Tokyo Metropolitan Government, 2015.

Gal'perin E. M. Water leaks in the distribution network 21

E. M. GAL'PERIN*

* Gal'perin Evgenii Moiseevich, Ph. D. (Engineering), Professor, Water Supply and Wastewater Disposal Department, Samara State University of Architecture and Civil Engineering

194 Molodogvardeiskaia str., 443001, Samara, Russian Federation, tel.: +7 (846) 339-14-11, e-mail: evg-galperin@yandex.ru

Ensuring the integrity of a water distribution network with hundreds kilometers of pressure pipelines laid underground sometimes in corrosive soil and ground water is practically impossible. Leaks in the water distribution network are a permanent element of the network operation and maintenance. Drinking water losses during transportation pose a tangible economic damage to water providers, contribute to underground water level increase, and sometimes produce an adverse environmental effect. The operation personnel carry out continuous work on eliminating water leaks. Water leak control in the distribution network is an essential part of operation and maintenance. The information on water leaks amount and water losses in certain countries of the world is presented. Detailed description of the experience in preventing leaks in the Tokyo water distribution network with the lowest in the world water leak level is presented.

Key words: water distribution network, water leaks and losses, pipeline, seismic consistency, diagnostic instruments.

REFERENCES

- [Method of determining unaccounted-for water and water losses in public water supply systems]. ZhKKh: Zhurnal Rukovoditelia i Glavnogo Bukhgaltera, 2006, no. 1, 2, 51 p. (In Russian).

- Lerner A. D. [Unaccounted-for water in public water supply and wastewater systems]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2005, no. 4, pp. 9–12. (In Russian).

- Lerner A. D., Domnin K. V., Boiko S. V., Kochetova M. G. [Justification of unaccounted-for water in water supply and wastewater management systems]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2012, no. 7, pp. 64–70. (In Russian).

- Hiroki Ariyoshi. Strategy for water leakage control in Japan. JWA Workshop of Water & Energy and Water Loss, 2014, 14 p.

- Beuken R. H. S., Lavooij C. S. W., Bosch A., Schaap P. G. Low leakage in the Netherlands Confirmed: Proceedings of the 8th Annual Water Distribution Systems Analysis Symposium (ASCE). USA, Cincinnati, 2006.

- Beecher J. A. Survey of State Agency Water Loss Reporting Practices. AWWA, Colorado, USA, 2002, 10 p.

- OFWAT. Service and delivery-performance of the water companies in England and Wales 2009–10 report. OFWAT. UK, 2010.

- Fantozzi M. Italian case study in applying IWA WLTF approach: results obtained: Eds. J. Thornton, R. Sturm, G. Kunkel. Water Loss Control. New York, McGraw-Hill, 2008, pp. 421–432.

- Marques R. C., Monteiro A. J. Application of performance indicators to control loses- results from the Portuguese water sector. Water Science and Technology: Water Supply, 2003, № 3 (1,5), pp. 127–133.

- Kanakoudis V., Tsitsifli S. Results of an urban water distribution network performance evaluation attempt in Greece. Urban Water Journal, 2010, № 7 (5), pp. 267–285.

- Carpenter Т., Lambert A., McKenzie R. Applying the IWA approach to water loss performance indicators in Australia. Water Science and Technology: Water Supply, 2003, № 3 (1/2), pp. 153–161.

- Zechner F. Time for a change. The Undergrounder, Ontario Sewer and Watermain Construction Association, 2007, p. 9.

- ADB. Every Drop Counts: Learning from Good Practices in Eight Asian Cities. Asian Development Bank, Manila, 2010.

- Cheung P. B., Girl G. V. Night now analysis and modeling for leakage estimation in a water distribution system. Integrating Water Systems: Eds. Boxall, Maksimovic. Taylor and Francis Group, London, 2009.

- Babic B., Dukin A., Stanic M. Managing water pressure for water savings in developing countries. Serbia, University of Belgrade, 2014, pp. 122–132.

- Welcome to Bureau of Waterworks, Tokyo Metropolitan Government. For Water Professionals, 2013. https://www.waterprofessionals.metro.tokyo.jp/ (accessed 22.04.2016).

- Mutikanga H. E. Water loss management: Tool and for development countries. Dissertation of degree of doctor to be defended. The Netherlands, June 4, 2012.

- Prevention of Water Leakage in Tokyo. Bureau of Waterworks, Tokyo Metropolitan Government, 2014.

- Leakage Prevention in Tokyo. Bureau of Waterworks, Tokyo Metropolitan Government, 2015.

ОЧИСТКА СТОЧНЫХ ВОД

УДК 628.316.12

Рублевская О. Н., Панкова Г. А., Леонов Л. В., Колосов Д. Е. Апробация искусственного алюмосиликатного сорбента «Глинт» для доочистки биологически очищенных коммунальных сточных вод 30

О. Н. РУБЛЕВСКАЯ1, Г. А. ПАНКОВА2, Л. В. ЛЕОНОВ3, Д. Е. КОЛОСОВ4

1 Рублевская Ольга Николаевна, заместитель директора по развитию, ГУП «Водоканал Санкт-Петербурга»

191015, Россия, Санкт-Петербург, Кавалергардская ул., 42, тел.: (812) 438-43-45, e-mail: Rublevskaya_ON@vodokanal.spb.ru

2 Панкова Гаяне Агасовна, директор по развитию, ГУП «Водоканал Санкт-Петербурга»

191015, Россия, Санкт-Петербург, Кавалергардская ул., 42, тел.: (812) 326-52-06, e-mail: Pankova_GA@vodokanal.spb.ru

3 Леонов Леонид Владимирович, технолог-консультант, Бюро развития систем водоснабжения и водоотведения, ГУП «Водоканал Санкт-Петербурга»

191015, Россия, Санкт-Петербург, Кавалергардская ул., 42, тел.: (812) 447-92-62, e-mail: Leonov_LV@vodokanal.spb.ru

4 Колосов Денис Евгеньевич, руководитель отдела внедрения и технического сопровождения, ООО «НПО «Завод химических реагентов»

150999, Россия, г. Ярославль, ул. Чайковского, 30, тел.: (4852) 67-44-80, e-mail: d.e.kolosov@yandex.ru

Приведены результаты пилотных испытаний синтетического алюмосиликатного сорбента под торговой маркой «Глинт» в сравнении с гранулированным активированным углем (ГАУ) марки АГ-3. Исследования проводились на очищенной воде Северной станции аэрации ГУП «Водоканал Санкт-Петербурга». В отобранных пробах воды определялись следующие показатели: рН, концентрация взвешенных веществ, фосфора фосфатов, анионных поверхностно-активных веществ, ионов железа, цинка, алюминия, никеля, меди и марганца. Сорбент «Глинт» является алюмосиликатным зернистым материалом с развитой поверхностью и содержит способные к обмену ионы кальция и магния. Материал «Глинт» неплохо зарекомендовал себя при очистке промышленных сточных вод, загрязненных ионами тяжелых металлов, но при этом не загрязненных органическими соединениями и веществами-комплексообразователями.

Ключевые слова: сточные воды, доочистка, тяжелые металлы, алюмосиликатный сорбент, активированный уголь, фильтрация.

WASTEWATER TREATMENT

Rublevskaia O. N., Pankova G. A., Leonov L. V., Kolosov D. E. Approbation of Glint artificial aluminosilicate sorbent for tertiary treatment of biologically treated domestic wastewater 30

O. N. RUBLEVSKAIA1, G. A. PANKOVA2, L. V. LEONOV3, D. E. KOLOSOV4

1 Rublevskaia Ol'ga Nikolaevna, Deputy Director for Development, SUE «Vodokanal of St. Petersburg»

42 Kavalergardskaia str., 191015, St. Petersburg, Russian Federation, tel.: +7 (812) 438-43-45, e-mail: Rublevskaya_ON@vodokanal.spb.ru

2 Pankova Gaiane Agasovna, Director for Development, SUE «Vodokanal of St. Petersburg»

42 Kavalergardskaia str., 191015, St. Petersburg, Russian Federation, tel.: + 7 (812) 326-52-06, e-mail: Pankova_GA@vodokanal.spb.ru

3 Leonov Leonid Vladimirovich, Consultant-Process Engineer, Bureau for Water Supply and Wastewater Disposal System Development, SUE «Vodokanal of St. Petersburg»

42 Kavalergardskaia str., 191015, St. Petersburg, Russian Federation, tel.: + 7 (812) 447-92-62, e-mail: Leonov_LV@vodokanal.spb.ru

4 Kolosov Denis Evgen'evich, Chief of Department for Implementation and Technical Support, «Chemical Agents Factory Scientific-Production Association» LLC

30 Tchaikovskogo str., 150999, Yaroslavl, Russian Federation, tel.: +7 (4852) 67-44-80, e-mail: d.e.kolosov@yandex.ru

The results of pilot tests of synthetic aluminosilicate sorbent under Glint trademark in comparison with AG-3 granulated activated carbon are presented. The study was carried out with effluent from the North Wastewater Treatment Plant of SUE «Vodokanal of St. Petersburg». The following parameters were determined in the effluent samples: рН, suspended solids concentration, phosphate as P, anionic surfactants, ions of iron, zinc, aluminium, nickel, copper and manganese. Glint sorbent is aluminosilicate granular material with effective surface and contains exchangeable ions of calcium and magnesium. Glint material proved itself in the treatment of industrial wastewater contaminated with heavy metal ions but not contaminated with organics and complexing compounds.

Key words: wastewater, tertiary treatment, heavy metals, aluminosilicate sorbent, activated carbon, filtration.

УДК 628.35:661.5

Лемэр Р., Кристенссон М., Жэо Х., Ле Нуар М., Вун К. Опыт запуска и эксплуатации биореакторов деаммонификации с подвижным слоем загрузки и испытание новой технологической схемы деаммонификации 38

Р. ЛЕМЭР1, М. КРИСТЕНССОН2, Х. ЖЭО3, М. ЛЕ НУАР4, К. ВУН5

1 Ромэн Лемэр, Veolia Water Technical Department

1 Giovanni Battista Pirelli, 94417, St.-Maurice, France

2 Магнус Кристенссон, AnoxKaldnes AB

11A Klosterängsvägen, 22647, Lund, Sweden

3 Хонг Жэо, Kruger Inc.

4001 Weston Parkway, 27513, Cary, NC, USA

4 М. Ле Нуар, AnoxKaldnes AB

11A Klosterängsvägen, 22647, Lund, Sweden

5 К. Вун, Veolia Water Solutions and Technologies

65 Pirrama Road, Bay Centre, Pyrmont NSW 2009, Australia

Исследован одноступенчатый процесс деаммонификации с использованием биопленки на подвижных носителях в реакторе полного перемешивания (ANITA™Mox). Частичная нитритация и автотрофное удаление азота происходят одновременно в пределах биопленки, где благодаря ограничению массопереноса кислорода возникают аэробные и аноксидные зоны. Аммонийокисляющие бактерии (AOB) окисляют NH4 до NO2 в аэробной зоне биопленки (внешняя часть), в то время как анаммокс-бактерии (AnAOB), расположенные в аноксидной зоне биопленки (внутренний слой), потребляют NO2, произведенный аммонийокисляющими бактериями, вместе с остаточным NH4. Процесс осуществлен в полномасштабной конфигурации биореактора с подвижным слоем загрузки (MBBR) для обработки сливной воды (возвратных потоков) от обезвоживания сброженного осадка. Запуск установок ускорили путем инокуляции – переноса 3–15% носителей из работающего реактора с установившейся AOB/AnAOB биопленкой, которые были смешаны со «свежими» носителями. В полномасштабном процессе скорость удаления азота составляла до 1,2 кг/(м3(сут). Достижимая скорость определяется переносом субстрата в биопленке и зависит от плотности и толщины биопленки, температуры, концентрации субстрата. Один из возможных способов повысить эффективность удаления азота состоит в увеличении скорости переноса субстрата. Использование интегрированного биореактора с фиксированной биопленкой (IFAS) позволяет пространственно разделить нитритацию и анаммокс-реакции в отличие от смежных процессов (в той же самой биопленке), обеспечивая аммонийокисляющим бактериям возможность расти во взвешенной фазе для более эффективного использования растворенного кислорода и способствуя адаптации биопленки в основном к анаммокс-реакции, обеспечивая более высокие скорости. В этом режиме могут использоваться более низкие концентрации растворенного кислорода в реакторе. Данные, полученные на полномасштабном биореакторе с подвижным слоем загрузки ANITA™Mox (MBBR) при обработке сливной воды от обезвоживания осадка, совместно с предварительными результатами работы опытного образца биореактора объемом 50 м3 с фиксированной биопленкой ANITA™Mox (IFAS) показали, что скорость удаления азота увеличилась до 3 раз по сравнению с результатами, получаемыми для конфигурации биореактора с подвижным слоем загрузки.

Ключевые слова: удаление азота, анаммокс-процесс, ANITA™Mox, интегрированный биореактор с фиксированной биопленкой (IFAS), биореактор с подвижным слоем загрузки (MBBR).

Lemaire R., Christensson M., Zhao H., Le Noir M., Voon C. Experience from start-up and operation of deammonification MBBR plants, and testing of a new deammonification IFAS configuration 38

R. LEMAIRE1, M. CHRISTENSSON2, H. ZHAO3, M. LE NOIR4, C. VOON5

1 Romain Lemaire, Veolia Water Technical Department

1 Giovanni Battista Pirelli, 94417, St.-Maurice, France

2 Magnus Christensson, AnoxKaldnes AB

11A Klosterängsvägen, 22647, Lund, Sweden

3 Hong Zhao, Kruger Inc.

4001 Weston Parkway, 27513, Cary, NC, USA

4 M. Le Noir, AnoxKaldnes AB

11A Klosterängsvägen, 22647, Lund, Sweden

5 C. Voon, Veolia Water Solutions and Technologies

65 Pirrama Road, Bay Centre, Pyrmont NSW 2009, Australia

A single-stage deammonification process utilizing biofilms on moving carriers in a mixed reactor (ANITA™Mox) is studied. Partial nitritation and autotrophic N-removal occur simultaneously within the biofilm, where aerobic and anoxic zones result from oxygen mass transfer limitation. Ammonium oxidizing bacteria (AOB) oxidize NH4 to NO2 in the aerobic zone of the biofilm (i. e. external biofilm) while Anammox bacteria (AnAOB) located in the anoxic zone of the biofilm (i. e. internal biofilm) consume NO2 produced by AOB together with the excess NH4. The process has been implemented at full-scale as a Moving Bed Biofilm Reactor (MBBR) to treat reject water from dewatering of digested sludge. Startup of these installations was accelerated using a seeding strategy whereby 3–15% of carriers with established AOB/AnAOB biofilm were mixed with new carriers. N-removal rates up to 1.2 kgN/(m3react(d) have been observed in the full-scale process. The achievable rate is influenced by substrate transport inside the biofilm, which depends on factors such as biofilm density, thickness, temperature, and substrate concentrations. One possible strategy to increase the N-removal is to enhance substrate transport. Using Integrated Fixed-Film Activate Sludge (IFAS) to separate the nitritation and anammox reactions spatially, instead of adjacent in the same biofilm, allows the AOB to grow in suspended phase to better utilize DO, while allowing the biofilm to specialize in AnAOB reaction to achieve higher rates. A lower bulk DO can be used in this mode. Results from full-scale ANITA™Mox MBBR treating sidestream effluent are presented together with preliminary ANITA™Mox IFAS results from a 50 m3 full-scale prototype showing an increase in N-removal rate of up to 3 times that usually achieved in pure MBBR configuration.

Keywords: nitrogen removal, Anammox, ANITA™Mox, IFAS, MBBR.

REFERENCES

- Chudoba P., Sardet C., Palko G., Guibelin E. Main factors influencing anaerobic digestion of sludge and energy efficiency at several large WWTP in central Europe. 2nd European Conference on Sludge Management. Budapest, Hungary, September, 2010.

- Abma W., Schultz C., Mulder J., van der Star W., Strous M., Tokutomi T., van Loosdrecht M. Fullscale granular sludge Anammox process. Water Science Technology, 2007, no. 55 (8/9), pp. 27–33.

- Wett B. Development and implementation of a robust Deammonification process. Water Science Technology, 2007, no. 56 (7), pp. 81–88.

- Vlaeminck S., Cloetens L., Carballa M., Boon N., Verstraete W. Granular biomass capable of partial nitritation and Anammox. Water Science Technology, 2008, no. 58 (5), pp. 1113–1120.

- Vazquez-Padin J., Pozo M., Jarpa M., Figueroa M., Franco A., Mosqueral-Corral A., Campos J. L., Mendez R. Treatment of anaerobic sludge digesters effluent by the Canon process in an air pulsing SBR. Journal of Hazardous Materials, 2009, no. 166, pp. 336–341.

- Rosenwinkel K., Cornelius A. Deammonification in the moving-bed process for the treatment of wastewater with high ammonia content. Chemical Engineering Technology, 2005, no. 28 (1), pp. 49–52.

- Cema G. Comparative study on different Anammox systems. Ph. D. Thesis, KTH Stockholm, 2009, 72 p.

- Wett B., Hell M., Nyhuis G., Puempel T., Takacs I., Murthy S. Syntrophy of aerobic and anaerobic ammonia oxidisers. Water Science Technology, 2010, no. 61 (8), pp. 1915–1922.

- Chen J., Ji Q., Zheng P., Chen T., Wang C., Mahmood Q. Floatation and control of granular sludge in a high-rate Anammox reactor. Water Research, 2010, no. 44 (11), pp. 3321–3338.

- Lindell P., Heinonen M. Critical parameters of the Demon process start-up and practical implementation. IWA Holistic Sludge Management conference. Västerås, Sweden, May, 2013.

- Lemaire R., Liviano I., Ekström S., Roselius C., Chauzy J., Thornberg D., Thirsing S., Deleris S. Single-stage Deammonification MBBR process for reject water sidestream treatment: investigation of start-up strategy and carriers design. WEF Nutrient Recovery and Management conference. Miami, January, 2011.

- Schneider Y., Beier M., Rosenwinkel K. Impact of seeding on the start-up of the deammonification process with different sludge systems. IWA conference on Nutrient Removal. Krakow, Poland, September, 2009.

- Mases M., Dimitrova I., Nyberg U., Gruvberg C., Anderson B. Experiences from MBBR post-denitrification process in long-term operation at 2 WWTPs. IWA/WEF Biofilm reactor technology conference. Portland, Oregon, USA, August, 2010.

- APHA. Standard methods for the examination of water and wastewater. 19th edn., American Public Health Association. Washington DC, USA, 1995.

- Christensson M., Ekström S., Andersson Chan A., Le Vaillant E., Lemaire R. Experience from start-ups of the first ANITA Mox plants. Water Science Technology, 2013, no. 67 (12), pp. 2677–2684.

- Gustavsson D. Biological sludge liquor treatment at municipal wastewater treatment plants: A review. Vatten, 2010, no. 66 (3), pp. 179–192.

- Kampschreur M., van der Star W., Wielders H., Mulder J., Jetten M., van Loosdrecht M. Dynamics of nitric oxide and nitrous oxide emission during full-scale reject water treatment. Water Research, 2008, no. 42 (3), pp. 812–826.

- Kampschreur M., Temminck H., Kleerebezem R., Jetten M., van Loosdrecht M. Nitrous oxide emissions during wastewater treatment. Water Research, 2009, no. 43 (17), pp. 4093–4103.

- Joss A., Salzgeber D., Eugster J., König R., Rottermann K., Burger S., Fabijan P., Leumann S., Mohn J., Siegrist H. Full-scale nitrogen removal from digester liquid with partial nitritation and Anammox in one SBR. Environmental Science Technology, 2009, no. 43, pp. 5301–5306.

- Weissenbacher N., Takacs I., Murthy S., Fuerhacker M., Wett B. Gaseous nitrogen and carbon emissions from a fullscale deammonification plant. Water Environmental Research, 2010, no. 82 (2), pp. 169–175.

- Gustavsson D. J. I., Jansen J. L. C. Dynamics of nitrogen oxides emission from a full-scale sludge liquor treatment plant with nitritation. Water Science Technology, 2011, no. 63 (12), pp. 2838–2845.

- Al-Sharekh H. A., Hamoda M. F. Removal of organics from WW using a novel biological hybrid system. Water Science Technology, 2001, no. 43 (1), pp. 321–326.

- Ødegaard H., Gisvold B., Strickland J. The influence of carrier size and shape in the moving bed Biofilm process. Water Science Techology, 2000, no. 41 (4–5), pp. 383–391.

- Wessman F., Tuegen E. Y., Zheng Q., He G., Welander T., Rusten B. Increasing the capacity for treatment of chemical plant wastewater by replacing existing suspended carrier media with Kaldnes Moving Bed™ media at a plant in Singapore. Water Science Technology, 2004, no. 49 (11–12), pp. 199–205.

- Paul E., Wolff D. B., Ochoa J., Ribeiro da Costa R. H. Recycled and virgin plastic carriers in hybrid reactors for wastewater treatment. Water Environmental Research, 2006, no. 79 (7), pp. 765–774.

- Zhao H., Lemaire R., Christensson M., Thesing G., Veuillet F., Ochoa J., Lamarre D., Gadbois A. Single-stage deammonification process performance – MBBR versus IFAS configurations. WEF/IWA Nutrient Removal and Recovery conference. Vancouver, Canada, July, 2013.

- Veuillet F., Lacroix S., Bausseron A., Gonidec E., Ochoa J., Christensson M., Lemaire R. IFAS ANITA™Mox process – a new perspective for advanced N-removal. 9th IWA conference on Biofilm Reactors. Paris, France, May, 2013.

ТРУБОПРОВОДНЫЕ СИСТЕМЫ

УДК 628.144:532.542

Продоус О. А., Терехов Л. Д. Сравнительная оценка использования таблиц разных авторов для гидравлического расчета трубопроводов из напорных полиэтиленовых труб 55

О. А. ПРОДОУС1, Л. Д. ТЕРЕХОВ2

1 Продоус Олег Александрович, доктор технических наук, профессор, генеральный директор ООО «Компания ИНКО»

190005, Россия, Санкт-Петербург, Московский проспект, 37/1, литера А, тел.: (812) 316-54-55, e-mail: encopspb@sp.ru

2 Терехов Лев Дмитриевич, доктор технических наук, профессор, заместитель генерального директора, ООО «Компания ИНКО»

190005, Россия, Санкт-Петербург, Московский проспект, 37/1, литера А, тел.: (812) 316-54-55, e-mail: encopspb@sp.ru

Сравниваются результаты гидравлических расчетов, проведенных с использованием таблиц разных авторов. Приводится пример гидравлического расчета трубопровода диаметром 160 мм для конкретного расхода и давления, а также анализ полученных гидравлических характеристик по таблицам разных авторов для гидравлического расчета напорных полиэтиленовых труб с практическими выводами. Необходимость такого сравнения продиктована запросами проектных организаций, разрабатывающих проекты трубопроводов из напорных полиэтиленовых труб и испытывающих трудности в выборе конкретных таблиц для проведения точного гидравлического расчета, а также наличием существенных погрешностей при определении удельных потерь напора по длине – гидравлического сопротивления, влияющего в итоге на величину затрат электроэнергии насосов при транспортировании воды.

Ключевые слова: гидравлический расчет, полиэтиленовые трубы, удельные потери напора, гидравлическое сопротивление, погрешность расчета.

СПИСОК ЛИТЕРАТУРЫ

- Шевелев Ф. А., Шевелев А. Ф. Таблицы для гидравлического расчета водопроводных труб: Справочное пособие. – М.: ООО «Издательский Дом БАСТЕТ», 2014. 384 с.

- Добромыслов А. Я. Таблицы для гидравлических расчетов трубопроводов из полимерных материалов. Т. 1. Напорные трубопроводы. – М., ВНИИМП, 2004. 209 с.

- Продоус О. А. Таблицы для гидравлического расчета труб напорных из полиэтилена: Справочное пособие. – СПб: Издательский дом Герда, 2011. 240 с.

- Тольцман В. Ф. Гидравлический расчет водопроводных труб // Водоснабжение и санитарная техника. 1959. № 5. С. 1–3.

PIPELINE SYSTEMS

Prodous O. A., Terekhov L. D. Comparative evaluation of using charts by different authors for hydraulic calculation of pressure polyethylene pipelines 55

O. A. PRODOUS1, L. D. TEREKHOV2

1 Prodous Oleg Aleksandrovich, Doctor of Engineering, Professor, General Director, «INKO Company» LLC

Build. A, 37/1 Moskovskii ave., 190005, St. Petersburg, Russian Federation, tel.: +7 (812) 316-54-55, e-mail: encopspb@sp.ru

2 Terekhov Lev Dmitrievich, Doctor of Engineering, Professor, Deputy General Director, «INKO Company» LLC

Build. A, 37/1 Moskovskii ave., 190005, St. Petersburg, Russian Federation, tel.: +7 (812) 316-54-55, e-mail: encopspb@sp.ru

The results of hydraulic calculations carried out with the use of charts compiled by different authors are compared. The example of hydraulic calculations of a pipeline with a diameter of 160 mm for certain flow rate and pressure as well as the analysis of the hydraulic characteristics obtained from the charts by different authors for hydraulic calculations of pressure polyethylene pipes with practical conclusions are presented. The demand for such a comparison is driven by the inquiries from engineering companies busy with designing pressure polyethylene pipelines and experiencing difficulties with choosing the right charts for precise hydraulic calculations; and by the significant errors in the process of determining specific head losses along the length – hydraulic resistance that ultimately influences energy consumption of pumps during water transportation.

Key words: hydraulic calculation, polyethylene pipes, specific head losses, hydraulic resistance, calculation error.

REFERENCES

- Shevelev F. A., Shevelev A. F. Tablitsy dlia gidravlicheskogo rascheta vodoprovodnykh trub: Spravochnoe posobie [Charts for hydraulic calculations of water pipelines: Reference aid. Moscow, BASTET Publ., 2014, 384 p.].

- Dobromyslov A. Ia. Tablitsy dlia gidravlicheskikh raschetov truboprovodov iz polimernykh materialov. T. 1. Napornye truboprovody [Charts for hydraulic calculations of pipelines made of polymer materials. V. 1. Pressure pipelines. Moscow, VNIIMP Publ., 2004, 209 p.].

- Prodous O. A. Tablitsy dlia gidravlicheskogo rascheta trub napornykh iz polietilena: Spravochnoe posobie [Charts for hydraulic calculations of pressure polyethylene pipelines: Reference aid. St. Petersburg, Gerda Publ., 2011, 240 p.].

- Tol'tsman V. F. [Hydraulic calculations of water pipelines]. Vodosnabzhenie i Sanitarnaia Tekhnika, 1959, no. 5, pp. 1–3. (In Russian).

НОВОЕ ОБОРУДОВАНИЕ

УДК 628.321

Жадан А. В., Касаточкин А. С., Ларионов С. Ю., Пантелеев А. А., Рябчиков Б. Е., Шилов М. М. Испытание опытно-промышленного высокоскоростного тонкослойного осветлителя ВТИ-М с микропеском 59

А. В. ЖАДАН1, А. С. КАСАТОЧКИН2, С. Ю. ЛАРИОНОВ3, А. А. ПАНТЕЛЕЕВ4, Б. Е. РЯБЧИКОВ5, М. М. ШИЛОВ6

1 Жадан Александр Владимирович, кандидат технических наук, генеральный директор ЗАО «Научно-производственная компания Медиана-Фильтр»

105318, Россия, Москва, Ткацкая ул., 1, тел.: (495) 660-07-71, e-mail: Jadan@mediana-filter.ru

2 Касаточкин Александр Сергеевич, инженер-исследователь, ЗАО «Научно-производственная компания Медиана-Фильтр»

105318, Россия, Москва, Ткацкая ул., 1, тел.: (926) 119-38-09, e-mail: kasatochkin@mediana-filter.ru

3 Ларионов Сергей Юрьевич, кандидат технических наук, начальник отдела НИОКР, ЗАО «Научно-производственная компания Медиана-Фильтр»

105318, Россия, Москва, Ткацкая ул., 1, тел.: (495) 660-07-71, e-mail: Larionov@mediana-filter.ru

4 Пантелеев Алексей Анатольевич, доктор физико-математических наук, руководитель направления технологии воды и топлива кафедры тепловых электрических станций, Национальный исследовательский университет «Московский энергетический институт»

111250, Россия, Москва, Красноказарменная ул., 14, тел.: (495) 660-07-71, e-mail: Panteleev@mediana-filter.ru

5 Рябчиков Борис Евгеньевич, доктор технических наук, ведущий научный сотрудник, Государственный научный центр РФ «Троицкий институт инновационных и термоядерных исследований»

142190, Россия, Москва, г. Троицк, ул. Пушковых, вл. 12, тел.: (916) 694-49-48, e-mail: riabchikov-45@yandex.ru

6 Шилов Михаил Михайлович, старший инженер-исследователь, ЗАО «Научно-производственная компания Медиана-Фильтр»

105318, Россия, Москва, Ткацкая ул., 1, тел.: (495) 660-07-71, e-mail: Shilov@mediana-eco.ru

Для отработки в опытно-промышленном масштабе технологии интенсифицированной коагуляционной очистки воды создан опытно-промышленный высокоскоростной осветлитель ВТИ-М с микропеском. Установка проектной производительностью до 30 м3/ч предназначена для очистки поверхностных, а также ливневых и сточных вод. Она спроектирована таким образом, что процесс очистки может проводиться либо с рециркуляцией сформированного осадка, либо с использованием мелкозернистого песчаного утяжелителя ВТИ-М. Осветлитель ВТИ-М обеспечивает стабильное качество воды, которое полностью удовлетворяет требованиям для подачи ее на ионообменное обессоливание.

Ключевые слова: осветлитель, коагуляция, микропесок, интенсифицированная очистка, рециркуляция песка, тонкослойный блок, коагулянт, флокулянт.

СПИСОК ЛИТЕРАТУРЫ

- Рябчиков Б. Е., Ларионов С. Ю., Пантелеев А. А., Шилов М. М. Исследование интенсифицированной коагуляционной очистки воды с использованием микропеска // Водоснабжение и санитарная техника. 2015. № 5. С. 14–22.

- Рябчиков Б. Е., Пантелеев А. А., Ларионов С. Ю., Жадан А. В., Шилов М. М. Оборудование для осадительных методов очистки воды. Ч. 1. Направления совершенствования отечественного оборудования // Водоснабжение и канализация. 2014. № 11–12. С. 62–75.

- Рябчиков Б. Е., Пантелеев А. А., Ларионов С. Ю., Жадан А. В., Шилов М. М. Оборудование для осадительных методов очистки воды. Ч. 2. Наиболее эффективные зарубежные решения // Водоснабжение и канализация. 2014. № 11–12. С. 76–84.

- ACTIFLO Совершенный осветлитель: www.actiflo.com; www.veoliawaterst.com; http://prom.lysoform.ua/Content/Resources/Manuals/Actiflo%20rus.pdf (дата обращения 22.04.2016).

- Презентация фирмы Veolia: http://technomaps.veoliawatertechnologies.com/actiflo/ru/actiflo_turbo.htm (дата обращения 22.04.2016).

- Enhanced High Rate Clarification Actiflo® Turbo: http://www.veoliawaterst.com.au/vwst-australia/ressources/files/1/16921,VWS-Australia-Actiflo-Turbo-Brochu.pdf (дата обращения 22.04.2016).

- ACTIFLO® Process For Drinking Water Treatment – Kruger: http://www.krugerusa.com/kruger-usa/ressources/documents/1/25603,ACTIFLODWBrochure2014.pdf (дата обращения 22.04.2016).

ADVANCED EQUIPMENT

Zhadan A. V., Kasatochkin A. S., Larionov S. Iu., Panteleev A. A., Riabchikov B. E., Shilov M. M. Testing VTI-M pilot high-rate lamella clarifier with microsand 59

A. V. ZHADAN1, A. S. KASATOCHKIN2, S. Iu. LARIONOV3, A. A. PANTELEEV4, B. E. RIABCHIKOV5, M. M. SHILOV6

1 Zhadan Aleksandr Vladimirovich, Ph. D. (Engineering), General Director, «Mediana-Filter Research and Production Company» CJSC

1 Tkatskaia str., 105318, Moscow, Russian Federation, tel.: +7 (495) 660-07-71, e-mail: Jadan@mediana-filter.ru

2 Kasatochkin Aleksandr Sergeevich, Research Engineer, «Mediana-Filter Research and Production Company» CJSC

1 Tkatskaia str., 105318, Moscow, Russian Federation, tel.: +7 (926) 119-38-09, e-mail: kasatochkin@mediana-filter.ru

3 Larionov Sergei Iur'evich, Ph. D. (Engineering), Chief of R&D Department, «Mediana-Filter Research and Production Company» CJSC

1 Tkatskaia str., 105318, Moscow, Russian Federation, tel.: +7 (495) 660-07-71, e-mail: Larionov@mediana-filter.ru

4 Panteleev Aleksei Anatol'evich, Doctor of Physical and Mathematical Sciences, Water and Fuel Technology Discipline Head, Thermal Power Plants Department, «Moscow Power Engineering Institute» National Research University

14 Krasnokazarmennaia str., 111250, Moscow, Russian Federation, tel.: +7 (495) 660-07-71, e-mail: Panteleev@mediana-filter.ru

5 Riabchikov Boris Evgen'evich, Doctor of Engineering, Senior Research Scientist, State Research Center of Russian Federation Troitsk Institute for Innovation & Fusion Research

12 Pushkovykh str., 142190, Troitsk, Moscow, Russian Federation, tel.: +7 (916) 694-49-48, e-mail: riabchikov-45@yandex.ru

6 Shilov Mikhail Mikhailovich, Senior Research Engineer, «Mediana-Filter Research and Production Company» CJSC

1 Tkatskaia str., 105318, Moscow, Russian Federation, tel.: +7 (495) 660-07-71, e-mail: Shilov@mediana-eco.ru

In order to test and adjust in pilot mode the technology of enhanced water coagulation a VTI-M pilot high-rate clarifier with microsand was designed. The installation with a capacity of up to 30 m3/h is designed for the purification of surface, storm and waste water. It is constructed in such a way that the purification process can be carried out either with recycling of generated sludge or with the use of VTI-M fine-grained sandy weighting material. VTI-M clarifier provides for the sustainable water quality that fully meets the requirements to the quality of water supplied to ion exchange desalination.

Key words: clarifier, coagulation, microsand, enhanced purification, sand recycling, lamella block, coagulant, flocculant.

REFERENCES

- Riabchikov B. E., Larionov S. Iu., Panteleev A. A., Shilov M. M. [Study of enhanced water coagulation with the use of microsand]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2015, no. 5, pp. 14–22. (In Russian).

- Riabchikov B. E., Panteleev A. A, Larionov S. Iu., Zhadan A. V., Shilov M. M. [Equipment for sedimentation methods of water treatment. P. 1. The trends of improving home-made equipment]. Vodosnabzhenie i Kanalizatsiia, 2014, no. 11–12, pp. 62–75. (In Russian).

- Riabchikov B. E., Panteleev A. A., Larionov S. Iu., Zhadan A. V., Shilov M. M. [Equipment for sedimentation methods of water treatment. P. 2. Most efficient international solutions]. Vodosnabzhenie i Kanalizatsiia, 2014, no. 11–12, pp. 76–84. (In Russian).

- ACTIFLO Perfect clarifier: www.actiflo.com; www.veoliawaterst.com; http://prom.lysoform.ua/Content/Resources/Manuals/Actiflo%20rus.pdf (accessed 22.04.2016).

- Veolia presentation: http://technomaps.veoliawatertechnologies.com/actiflo/ru/actiflo_turbo.htm (accessed 22.04.2016).

- Enhanced High Rate Clarification Actiflo® Turbo: http://www.veoliawaterst.com.au/vwst-australia/ressources/files/1/16921,VWS-Australia-Actiflo-Turbo-Brochu.pdf (accessed 22.04.2016).

- ACTIFLO® Process For Drinking Water Treatment – Kruger: http://www.krugerusa.com/kruger-usa/ressources/documents/1/25603,ACTIFLODWBrochure2014.pdf (accessed 22.04.2016).

НАДЕЖНОСТЬ СЕТЕЙ

УДК 628.14:62-192

Ермолин Ю. А., Алексеев М. И. Учет «старения» объекта при оценке его надежности 68

Ю. А. ЕРМОЛИН1, М. И. АЛЕКСЕЕВ2

1 Ермолин Юрий Александрович, доктор технических наук, профессор, Московский государственный университет путей сообщения

127994, Россия, Москва, ул. Образцова, 9, стр. 9, тел.: (495) 684-21-68, e-mail: ermolin.y@yandex.ru

2 Алексеев Михаил Иванович, доктор технических наук, профессор, академик Российской академии архитектуры и строительных наук, Санкт-Петербургский государственный архитектурно-строительный университет

190005, Россия, Санкт-Петербург, 2-я Красноармейская ул., 4, тел.: (812) 316-72-97, e-mail: m.i.alexeev@mail.ru

Обсуждаются вопросы, связанные с оценкой надежности нестационарных (стареющих) объектов, для которых характерно возрастание интенсивности отказов с течением времени. Констатируется практическое отсутствие методик, которые могли бы быть использованы в инженерных расчетах по оценке надежности таких объектов. Предлагается метод, состоящий в формальной замене нестационарного объекта фиктивным стационарным, постоянное значение интенсивности отказов которого подбирается из некоторых дополнительных соображений. Получены удобные для практического применения соотношения, выражающие показатель надежности фиктивного объекта через параметры характеристики старения реального нестационарного объекта.

Ключевые слова: нестационарность, показатель надежности, фиктивная замена объекта, критерий замены, вероятность безотказной работы, методика расчета.

СПИСОК ЛИТЕРАТУРЫ

- Вентцель Е. С. Исследование операций: задачи, принципы, методология. – М.: Наука, 1986. 208 с.

- Гнеденко Б. В., Беляев Ю. К., Соловьев А. Д. Математические методы в теории надежности. – М.: Наука, 1965. 524 с.

- Алексеев М. И., Ермолин Ю. А. Надежность сетей и сооружений систем водоотведения. – М.: Издательство АСВ, 2015. 196 с.

- Huzurbazar A. V., Briand D., Cranwell R. Statistical reliability with applications to defense / Reliability engineering advances: Ed. by Gregory I. Hayworth. – New York: Nova Science Publishers, Inc., 2009. Р. 45–75.

- Баранов Л. А., Ермолин Ю. А. Оценка показателей надежности «линейно-стареющего» объекта // Надежность. 2015. № 4 (55). С. 57–60.

- Ermolin Yuri A. Reliability estimation of urban wastewater disposal networks / Reliability engineering advances: Ed. by Gregory I. Hayworth. – New York: Nova Science Publishers, Inc., 2009. Р. 379–397.

NETWORK RELIABILITY

Ermolin Iu. A., Alekseev M. I. Consideration of object ageing in estimating its reliability 68

Iu. A. ERMOLIN1, M. I. ALEKSEEV2

1 Ermolin Iurii Aleksandrovich, Doctor of Engineering, Professor, Moscow State University of Railway Engineering

Build. 9, 9 Obraztsova str., 127994, Moscow, Russian Federation, tel.: +7 (495) 684-21-68, e-mail: ermolin.y@yandex.ru

2 Alekseev Mikhail Ivanovich, Doctor of Engineering, Professor, Academician, Russian Academy of Architecture and Construction Sciences, Saint-Petersburg State University of Architecture and Civil Engineering

4, 2nd Krasnoarmeiskaia str., 190005, St. Petersburg, Russian Federation, tel.: + 7 (812) 316-72-97, e-mail: m.i.alexeev@mail.ru

The issues related to the estimation of reliability of nonstationary (ageing) objects that are characterized by increasing failure rate with time are discussed. The lack of methods that could be used in engineering evaluation of the reliability of these objects is stated. The method is suggested that consists in nominal replacing the nonstationary object with fictive stationary one with failure rate constant value that is selected basing on several additional considerations. The relationships readily usable in practice and expressing the reliability index of the fictive objects through the parameters of the ageing characteristics of the actual nonstationary objects were obtained.

Key words: nonstationarity, reliability index, fictive replacement of objects, replacement criterion, probability of failure-free operation, calculation method.

REFERENCES

- Venttsel' E. S. Issledovanie operatsii: zadachi, printsipy, metodologiia [Study of operations: tasks, principles, methodology. Moscow, Nauka Publ., 1986, 208 p.].

- Gnedenko B. V., Beliaev Iu. K., Solov'ev A. D. Matematicheskie metody v teorii nadezhnosti [Mathematical methods in the theory of reliability. Moscow, Nauka Publ., 1965, 524 p.].

- Alekseev M. I., Ermolin Iu. A. Nadezhnost' setei i sooruzhenii sistem vodootvedeniia [Reliability of wastewater disposal networks and facilities. Moscow, ASV Publ., 2015, 196 p.].

- Huzurbazar A. V., Briand D., Cranwell R. Statistical reliability with applications to defense. Reliability engineering advances: Ed. by Gregory I. Hayworth. New York, Nova Science Publishers, Inc., 2009, pp. 45–75.

- Baranov L. A., Ermolin Iu. A. [Estimation of reliability indices of a «linearly-ageing» object]. Nadezhnost’, 2015, no. 4 (55), pp. 57–60. (In Russian).

- Ermolin Yuri A. Reliability estimation of urban wastewater disposal networks. Reliability engineering advances. Ed. by Gregory I. Hayworth. New York, Nova Science Publishers, Inc., 2009, pp. 379–397.