ПИТЬЕВОЕ ВОДОСНАБЖЕНИЕ

УДК 628.161:544.723

Гвоздев В. А., Портнова Т. М., Яциневич Н. В. Восстановление сорбционной способности гранулированного активированного угля 4

В. А. ГВОЗДЕВ1, Т. М. ПОРТНОВА2, Н. В. ЯЦИНЕВИЧ3

1 Гвоздев Владимир Андреевич, заместитель директора департамента технологического развития и охраны окружающей среды, ГУП «Водоканал Санкт-Петербурга»

191015, Россия, Санкт-Петербург, Кавалергардская ул., 42, тел.: (812) 438-43-26, e-mail: Gvozdev_VA@vodokanal.spb.ru

2 Портнова Татьяна Михайловна, начальник службы главного технолога филиала «Водоснабжение Санкт-Петербурга», ГУП «Водоканал Санкт-Петербурга»

194156, Россия, Санкт-Петербург, Манчестерская ул., 1, тел.: (921) 762-32-65, e-mail: Portnova_TM@vodokanal.spb.ru

3 Яциневич Николай Владимирович, старший мастер участка очистных сооружений Северной водопроводной станции, Территориальное управление водоснабжения «Северное» филиала «Водоснабжение Санкт-Петербурга», ГУП «Водоканал Санкт-Петербурга»

195298, Россия, Санкт-Петербург, деревня Заневка, тел.: (812) 447-92-37, e-mail: Yacinevich_NY@vodokanal.spb.ru

Анализ показателей качества воды реки Невы свидетельствует об изменении химического, биологического и физического состава воды в результате внешних воздействий. В водоисточник попадают как микробиологические, так и органические химические загрязнения. Из всех контролируемых показателей качества питьевой воды неприятный запах потребитель определяет сразу. Двухслойная фильтрующая загрузка (песок и активированный уголь) позволяет эффективно удалять коллоидные соединения и мелкодисперсные частицы с низкой гидравлической крупностью. При этом слой гранулированного активированного угля удаляет различные органические соединения и водорастворимые нефтепродукты. Благодаря процессу окисления (деструкции) химических соединений с помощью озонирования и последующей обработке сорбентом удаляются органические вещества, придающие воде привкус и запах, а также (в небольшой степени) снижается цветность и перманганатная окисляемость. При использовании порошкообразного активированного угля на фильтрационных сооружениях требуется достижение эффективности очистки и оценка затрат, поскольку в том случае, если хлорсодержащий реагент вводится в воду сразу после его добавления, то существенно увеличиваются расходы реагентов на обеззараживание. Таким образом, очень важно включать в состав сооружений блок сорбционной очистки, где для повышения надежности обработки воды используется гранулированный активированный уголь. Проанализирована эффективность очистки воды с применением гранулированного активированного угля в условиях блока К-6 Южной водопроводной станции Санкт-Петербурга. Произведена оценка параметров очищенной воды после реактивации угля. Реактивация активированного угля марки Filtrasorb TL 830 при выбранных технологических режимах обеспечивает удовлетворительное восстановление сорбционных свойств материала при сохранении его механических характеристик.

Ключевые слова: водоподготовка, питьевая вода, cорбция, сорбент, гранулированный активированный уголь, порошкообразный активированный уголь, реактивация.

СПИСОК ЛИТЕРАТУРЫ

- Кинхле Х., Бадер Э. Активные угли и их промышленное применение. – Л.: Химия, 1984. 216 с.

- Дикаревский В. С., Медведев Г. П., Кармазинов Ф. В. Водоснабжение Санкт-Петербурга. – СПб.: Новый журнал, 2003. 688 с.

- Когановский А. М., Левченко Т. М., Кириченко В. А., Рода И. Г. Адсорбция органических веществ из воды. – Л.: Химия, 1990. 256 с.

- Николадзе Г. И., Сомов М. А. Водоснабжение. – М.: Стройиздат, 1995. 688 с.

DRINKING WATER SUPPLY

Gvozdev V. A., Portnova T. M., Iatsinevich N. V. Regeneration of the sorption capacity of granulated activated carbon 4

V. A. GVOZDEV1, T. M. PORTNOVA2, N. V. IATSINEVICH3

1 Gvozdev Vladimir Andreevich, Deputy Director, Department for Technologic Development and Environmental Protection, SUE «Vodokanal of St. Petersburg»

42 Kavalergardskaia St., 191015, Saint-Petersburg, Russian Federation, tel.: + 7 (812) 438-43-26, e-mail: Gvozdev_VA@vodokanal.spb.ru

2 Portnova Tat'iana Mikhailovna, Chief of the Chief Process Engineer Service, «Water Supply» Branch, SUE «Vodokanal of St. Petersburg»

1 Manchesterskaia St., 194156, Saint-Petersburg, Russian Federation, tel.: +7 (921) 762-32-65, e-mail: Portnova_TM@vodokanal.spb.ru

3 Iatsinevich Nikolai Vladimirovich, Senior Area Supervisor, Treatment Facilities, Northern Waterworks, «Northern» Territorial Office, «Water Supply» Branch, SUE «Vodokanal of St. Petersburg»

Zanevka Village, 195298, Saint-Petersburg, Russian Federation, tel.: +7 (812) 447-92-37, e-mail: Yacinevich_NY@vodokanal.spb.ru

The analysis of the Neva River water quality parameters shows the changes in the chemical, biological and physical composition of the water under the environmental impact. Microbial as well as organic chemical pollutants get into the water source. Among all the monitored drinking water quality indicators the customers recognize bad smell at once. Double-layer filter bed (sand and activated carbon) provides for the efficient removal of colloid compounds and finely dispersed particles with low hydraulic size. Herewith the granulated carbon layer traps various organic compounds and water soluble oil products. Owing to the process of chemical compound oxidation (destruction) by ozonation and subsequent treatment with sorbent the chemical substances that flavor water with taste and smell are removed; as well as the color and permanganate value are lowered. When using powdered activated carbon at the filtration facilities achieving the treatment efficiency and estimation of the costs are required because in case chlorine-containing chemical is added to the water immediately after activated carbon is introduced the consumption of disinfection chemicals significantly increases. Thus, it is very important to include a sorption unit with granulated activated carbon to improve the reliability of water treatment. The efficiency of water treatment with granulated activated carbon was tested in K-6 unit at the Southern Waterworks of Saint-Petersburg. The evaluation of the water quality parameters after carbon reactivation was made. Reactivation of Filtrasorb TL 830 activated carbon under the selected process conditions provides for the satisfactory regeneration of the material sorption capacity while preserving its mechanical properties.

Key words: water purification, drinking water, sorption, sorbent, granulated activated carbon, powdered activated carbon, reactivation.

REFERENCES

- Kinkhle H., Bader E. Aktivnye ugli i ikh promyshlennoe primenenie [Activated carbons and their use in industry. Leningrad, Khimiia Publ., 1984, 216 p.].

- Dikarevskii V. S., Medvedev G. P., Karmazinov F. V. Vodosnabzhenie Sankt-Peterburga [Water supply of Saint-Petersburg. Saint-Petersburg, Novyi Zhurnal Publ., 2003, 688 p.].

- Koganovskii A. M., Levchenko T. M., Kirichenko V. A., Roda I. G. Adsorbtsiia organicheskikh veshchestv iz vody [Adsorption of organic substances from water. Leningrad, Khimiia Publ., 1990, 256 p.].

- Nikoladze G. I., Somov M. A. Vodosnabzhenie [Water supply. Moscow, Stroiizdat Publ., 1995, 688 p.].

РОССИЙСКАЯ АССОЦИАЦИЯ ВОДОСНАБЖЕНИЯ И ВОДООТВЕДЕНИЯ

УДК 628.1/.2:336.7

Баженов В. И., Пупырев Е. И., Самбурский Г. А., Березин С. Е. Разработка методики расчета стоимости жизненного цикла оборудования, систем и сооружений для водоснабжения и водоотведения 10

В. И. БАЖЕНОВ1, Е. И. ПУПЫРЕВ2, Г. А. САМБУРСКИЙ3, С. Е. БЕРЕЗИН4

1 Баженов Виктор Иванович, доктор технических наук, профессор, исполнительный директор, ЗАО «Водоснабжение и водоотведение»; руководитель секции Экспертно-технологического совета Российской ассоциации водоснабжения и водоотведения

127018, Россия, Москва, Полковая ул., 1, тел.: (495) 641-00-41, e-mail: info@pump.ru

2 Пупырев Евгений Иванович, доктор технических наук, профессор, президент Межрегионального союза проектировщиков; председатель Экспертно-технологического совета Российской ассоциации водоснабжения и водоотведения

119334, Россия, Москва, Ленинский проспект, 38, корп. 2, e-mail: e.pupyrev@gmail.com

3 Самбурский Георгий Александрович, кандидат технических наук, заместитель исполнительного директора, ученый секретарь Экспертно-технологического совета Российской ассоциации водоснабжения и водоотведения; доцент кафедры «Экологическая и промышленная безопасность», Институт тонких химических технологий им. М. В. Ломоносова, Московский технологический университет

119334, Россия, Москва, Ленинский проспект, 38, корп. 2, тел.: (495) 939-19-36, e-mail: gesamb@yandex.ru

4 Березин Сергей Евгеньевич, генеральный директор ЗАО «Водоснабжение и водоотведение»; эксперт Экспертно-технологического совета Российской ассоциации водоснабжения и водоотведения

127018, Россия, Москва, Полковая ул., 1, тел.: (495) 641-00-41, e-mail: info@pump.ru

Экспертно-методическим советом Российской ассоциации водоснабжения и водоотведения разработана «Методика расчета стоимости жизненного цикла оборудования, систем и сооружений водоснабжения и водоотведения». Методика была представлена на Х Конференции водоканалов России (19–22 сентября 2017 г., Калининград) и в настоящее время проходит согласование в Федеральной антимонопольной службе. Приведен анализ методик оценки стоимости жизненного цикла – зарубежных (на предмет соответствия государственным закупкам) и отечественных (их применение не имеет системного характера). Представлены расчетные зависимости, в том числе с учетом дисконтирования затрат текущей стоимости во времени. Приведены категории принадлежности объекта расчета: первая – оборудование, товар; вторая – объект капитального строительства. Адаптация расчетных показателей к международной практике сопровождается поддержкой общепринятой аббревиатуры, что упрощает процедуру участия зарубежных представителей в российских конкурсах. Приведены ссылки на примеры апробации расчетов СЖЦ в соответствии с функциональными особенностями разработанной методики по техническому и технологическому аспектам, а также по проектам – научно-исследовательским и опытно-конструкторским, государственно-частное партнерство, энергосервисный и лизинговый контракты.

Ключевые слова: водоснабжение, водоотведение, стоимость жизненного цикла, методика оценки, дисконтирование затрат.

СПИСОК ЛИТЕРАТУРЫ

- Составление технико-экономической части проектов внеплощадочных систем водоснабжения и канализации: Справочное пособие к СНиП / Союзводоканалпроект. – М.: Стройиздат, 1991. 102 с.

- Pump life cycle costs: A guide to LCC analysis for pumping systems: Edited by L. Frenning. – New Jersey, Hydraulic Institute Europump, 2001. 194 p.

- Березин С. Е. Цена или энергозатраты? Выбор оборудования на конкурсах должен осуществляться по совокупной стоимости пользования // Наилучшие доступные технологии водоснабжения и водоотведения. 2015. № 2. С. 36–40.

- Нефедова Е. Д., Хямяляйнен М. М., Ковжаровская И. Б. Опыт оценки эффективности мероприятий инвестиционной программы предприятия водопроводно-канализационного хозяйства // Водоснабжение и санитарная техника. 2017. № 3. С. 66–70.

- Баженов В. И., Березин С. Е., Зубовская Н. Н. Экономический анализ насосных систем на базе показателя – затраты жизненного цикла // Водоснабжение и санитарная техника. 2006. № 3, ч. 2. С. 31–35.

- Кармазинов Ф. В., Мельник Е. А., Ипатко М. Н., Ильин Ю. А., Игнатчик В. С., Игнатчик С. Ю. Методика оценки экономической эффективности систем подачи воды с насосными станциями, оборудованными резервуарами // Водоснабжение и санитарная техника. 2014. № 12. С. 48–54.

- Гуринович А. Д., Сычева Е. А. Методика оценки стоимости жизненного цикла водозаборной скважины // Вода Magazine. 2016. № 3 (103). С. 44–47.

- Гогина Е. С., Гуринович А. Д. Применение методики LСС для оценки эффективности инвестиционных проектов сооружений очистки сточных вод // Водоснабжение и санитарная техника. 2016. № 9. С. 36–41.

- Баженов В. И., Кривощекова Н. А. Экономический анализ систем биологической очистки сточных вод на основе показателя – затраты жизненного цикла // Водоснабжение и санитарная техника. 2009. № 2. С. 69–74.

- Баженов В. И., Березин С. Е., Устюжанин А. В. Совокупная стоимость владения – экономически обоснованный критерий выбора оборудования и технических решений // Наилучшие доступные технологии водоснабжения и водоотведения. 2014. № 4. С. 38–47.

- Баженов В. И., Березин С. Е., Устюжанин А. В. Обоснование строительства воздуходувных станций на базе экономического анализа затрат жизненного цикла // Водоснабжение и санитарная техника. 2015. № 2. С. 46–53.

- Баженов В. И., Устюжанин А. В. Оценка долгосрочных инвестиционных проектов с энергоэффективными решениями на основе показателя затраты жизненного цикла // Вестник МГСУ. 2015. № 9. С. 146–157.

- Щевелева Т. И. Методология учета эколого-экономических факторов при обращении с отходами // Вестник Московского университета. Серия 6: Экономика. 2013. № 6. С. 99–106.

- Воронцова Ю. В., Корчагина А. П. Life cycle costing как система формирования затрат на НИОКР // Вестник Университета (Государственный университет управления). 2017. № 9. С. 85–90.

- Кузнецова В. Б. Повышение эффективности мониторинга послепродажного обслуживания наукоемких изделий с целью снижения стоимости полного жизненного цикла // Альманах молодой науки. 2016. № 1. С. 22–26.

- Вьюнов С. С. Применение анализа стоимости жизненного цикла для проектов государственно-частного партнерства // Экономика и предпринимательство. 2016. № 11–1 (76–1). С. 371–374.

- Березин С. Е., Устюжанин А. В., Баженов В. И., Кукса М. А., Петров В. И., Петров Ю. В., Овсейчук Б. В., Носкова И. А. Бизнес-процесс энергосервисного договора (для крупного энергоузла на примере воздуходувных станций) // Наилучшие доступные технологии водоснабжения и водоотведения. 2016. № 1. С. 48–55.

- Березин С. Е., Баженов В. И., Устюжанин А. В., Кукса М. А., Петров В. И., Петров Ю. В., Овсейчук Б. В., Носкова И. А. Бизнес-процесс энергосервисного договора (для крупного энергоузла на примере воздуходувных станций) // Наилучшие доступные технологии водоснабжения и водоотведения. 2016. № 2. С. 43–48.

RUSSIAN WATER AND WASTEWATER ASSOCIATION

Bazhenov V. I., Pupyrev E. I., Samburskii G. A., Berezin S. E. Development of the method of life cycle costing of the equipment, systems and facilities for water supply and wastewater disposal 10

V. I. BAZHENOV1, E. I. PUPYREV2, G. A. SAMBURSKII3, S. E. BEREZIN4

1 Bazhenov Viktor Ivanovich, Doctor of Engineering, Professor, Executive Director, «Vodosnabzhenie i Vodootvedenie» CJSC; Section Leader of Expert-Technological Board, Russian Water and Wastewater Association

1 Polkovaia St., 127018, Moscow, Russian Federation, tel.: +7 (495) 641-00-41, e-mail: info@pump.ru

2 Pupyrev Evgenii Ivanovich, Doctor of Engineering, Professor, President of Transregional Association of Design Engineers; Chairman of Expert-Technological Board, Russian Water and Wastewater Association

Build. 2, 38 Leninskii Ave., 119334, Moscow, Russian Federation, e-mail: e.pupyrev@gmail.com

3 Samburskii Georgii Aleksandrovich, Ph. D. (Engineering), Deputy Executive Director, Scientific Secretary of Expert-Technological Board, Russian Water and Wastewater Association; Associate Professor, «Environmental and Industrial Safety» Department, Lomonosov Institute of Fine Chemical Technologies, Moscow Technological University

Build. 2, 38 Leninskii Ave., 119334, Moscow, Russian Federation, tel.: +7 (495) 939-19-36, e-mail: gesamb@yandex.ru

4 Berezin Sergei Evgen'evich, General Director, «Vodosnabzhenie i Vodootvedenie» CJSC; Expert of Expert-Technological Board, Russian Water and Wastewater Association

1 Polkovaia St., 127018, Moscow, Russian Federation, tel.: +7 (495) 641-00-41, e-mail: info@pump.ru

The Expert-Technological Board of the Russian Water and Wastewater Association has developed «The method of life cycle costing of the equipment, systems and facilities for water supply and wastewater disposal». The method was presented at X Conference of Russian Vodokanals (September 19–22, 2017, Kaliningrad), and at the present moment it is under approval of the Federal Anti-Monopoly Service. The analysis of the life cycle cost estimate methods – international (for the purpose of the compliance with the state procurements) and domestic (their use is not of system character). The calculation dependencies are presented also with account of discounting expenditures of the current cost in time. The categories of pertainance of the calculation objective are presented: the first – equipment, products; the second – capital construction projects. The adaptation of the estimate indicators to the international practice is accompanied with the support of the generally accepted abbreviation to simplify the procedure of the foreign representatives participating in the Russian tenders. The references to the examples of the approbation of the life cycle cost calculation in accordance with the functional specific features of the developed method related to the technical and technologic aspects as well as to the projects – research and design and experimental, public-private partnership, performance and leasing contracts are given.

Key words: water supply, wastewater disposal, life cycle cost, estimation procedure, discounting expenditures.

REFERENCES

- Sostavlenie tekhniko-ekonomicheskoi chasti proektov vneploshchadochnykh sistem vodosnabzheniia i kanalizatsii [Drawing up a feasibility study of the projects of offsite water supply systems and sewers. Reference guide to SNiP / Soiuzvodokanalproekt. Moscow, Stroiizdat Publ., 1991, 102 p.].

- Pump life cycle costs. A guide to LCC analysis for pumping systems. Edited by L. Frenning. New Jersey, Hydraulic Institute Europump, 2001, 194 p.

- Berezin S. E. [Cost or energy expenditures? Selection of the equipment during tenders shall be performed by the aggregate cost of use]. Nailuchshie Dostupnye Tekhnologii Vodosnabzheniia i Vodootvedeniia, 2015, no. 2, pp. 36–40. (In Russian).

- Nefedova E. D., Khiamialiainen M. M., Kovzharovskaia I. B. [The experience of evaluating the efficiency of the actions of the investment program of a water supply and wastewater disposal enterprise]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2017, no. 3, pp. 66–70. (In Russian).

- Bazhenov V. I., Berezin S. E., Zubovskaia N. N. [Ecomonic analysis of the pump systems based on the life cycle costs indicator ]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2006, no. 3, part 2, pp. 31–35. (In Russian).

- Karmazinov F. V., Mel'nik E. A., Ipatko M. N., Il'in Iu. A., Ignatchik V. S., Ignatchik S. Iu. [The method of evaluating the economic efficiency of water supply systems with pumping stations equipped with tanks]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2014, no. 12, pp. 48–54. (In Russian).

- Gurinovich A. D., Sycheva E. A. [The method of evaluating the life cycle cost of a water well]. Voda Magazine, 2016, no. 3 (103), pp. 44–47. (In Russian).

- Gogina E. S., Gurinovich A. D. [The use of LСС method in evaluating the efficienc y of investment projects of wastewater treatment facilities]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2016, no. 9, pp. 36–41. (In Russian).

- Bazhenov V. I., Krivoshchekova N. A. [Economic efficiency of the biological wastewater treatment facilities based on the life cycle costs indicator]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2009. no. 2, pp. 69–74. (In Russian).

- Bazhenov V. I., Berezin S. E., Ustiuzhanin A. V. [Total cost of ownership – the economically substantiated criterion of selecting equipment and technical solutions]. Nailuchshie Dostupnye Tekhnologii Vodosnabzheniia i Vodootvedeniia, 2014, no. 4, pp. 38–47. (In Russian).

- Bazhenov V. I., Berezin S. E., Ustiuzhanin A. V. [Feasibility of air-blower house construction on the basis of life cycle costs evaluation]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2015, no. 2, pp. 46–53. (In Russian).

- Bazhenov V. I., Ustiuzhanin A. V. [Assessment of long-term investment projects with energy efficient solutions on the basis of life cycle costs indicator]. Vestnik MGSU, 2015, no. 9, pp. 146–157. (In Russian).

- Shcheveleva T. I. [Methodology of environmental-economic factors recognition in waste handling]. Vestnik Moskovskogo Universiteta. Seriia 6. Ekonomika, 2013, no. 6. pp. 99–106. (In Russian).

- Vorontsova Iu. V., Korchagina A. P. [Life cycle costing as a system of calculating expenditures on research and development activities]. Vestnik Universiteta (Gosudarstvennyi Universitet Upravleniia), 2017, no. 9, pp. 85–90. (In Russian).

- Kuznetsova V. B. [Improving the efficiency of monitoring after-sale service of scientific products with the purpose of decreasing the full life cycle cost]. Al'manakh Molodoi Nauki, 2016, no. 1, pp. 22–26. (In Russian).

- V'iunov S. S. [Using life cycle cost analysis for public-private partnership projects]. Ekonomika i Predprinimatel'stvo, 2016, no. 11–1 (76–1), pp. 371–374. (In Russian).

- Berezin S. E., Ustiuzhanin A. V., Bazhenov V. I., Kuksa M. A., Petrov V. I., Petrov Iu. V., Ovseichuk B. V., Noskova I. A. [Business-process of a performance contract (for a big electric generation system through the example of air-blower plants)]. Nailuchshie Dostupnye Tekhnologii Vodosnabzheniia i Vodootvedeniia, 2016, no. 1, pp. 48–55. (In Russian).

- Berezin S. E., Bazhenov V. I., Ustiuzhanin A. V., Kuksa M. A., Petrov V. I., Petrov Iu. V., Ovseichuk B. V., Noskova I. A. [Business-process of a performance contract (for a big electric generation system through the example of air-blower plants)]. Nailuchshie Dostupnye Tekhnologii Vodosnabzheniia i Vodootvedeniia, 2016, no. 2, pp. 43–48. (In Russian).

ОЧИСТКА СТОЧНЫХ ВОД

УДК 628.33:665.622.43

Урмитова Н. С., Абитов Р. Н., Низамова А. Х., Хабибуллин Р. Р. Использование крупнозернистых коалесцирующих материалов в установках очистки нефтепромысловых сточных вод 20

Н. С. УРМИТОВА1, Р. Н. АБИТОВ2, А. Х. НИЗАМОВА3, Р. Р. ХАБИБУЛЛИН4

1 Урмитова Назия Салиховна, кандидат технических наук, доцент кафедры «Водоснабжение и водоотведение», Казанский государственный архитектурно-строительный университет

420043, Россия, г. Казань, Зеленая ул., 1, тел.: (843) 510-46-97, e-mail: kgasu.viv@gmail.com

2 Абитов Рунар Назилович, кандидат педагогических наук, заведующий кафедрой «Водоснабжение и водоотведение», Казанский государственный архитектурно-строительный университет

420043, Россия, г. Казань, Зеленая ул., 1, тел.: (843) 510-46-97, e-mail: kgasu.viv@gmail.com

3 Низамова Аида Ханифовна, старший преподаватель кафедры «Водоснабжение и водоотведение», Казанский государственный архитектурно-строительный университет

420043, Россия, г. Казань, Зеленая ул., 1, тел.: (843) 510-46-97, e-mail: kgasu.viv@gmail.com

4 Хабибуллин Рафиль Рафисович, инженер производственно-технического отдела, Управляющая компания «Жилище и комфорт»

420100, Россия, г. Казань, ул. Академика Глушко, 8, тел.: (843) 221-31-50, e-mail: info@ukgik.ru

Республика Татарстан относится к субъектам Российской Федерации с высоким уровнем развития промышленности, в частности нефтехимической, нефтедобывающей и нефтеперерабатывающей. На объектах нефтедобывающей промышленности образуется большое количество нефтесодержащих сточных вод. Эффективным методом их утилизации является повторное использование для заводнения нефтяных пластов с целью увеличения нефтеотдачи. Перед закачкой в пласт из сточных вод необходимо удалить нефть и механические примеси. Для этого широко применяется метод отстаивания. Для интенсификации процесса используется предварительная обработка сточных вод. Одним из наиболее эффективных методов является процесс коалесценции с применением гранулированных коалесцирующих насадок. С целью интенсификации процесса очистки разработаны гранулированные коалесцирующие материалы на основе полимеров и керамзита. В результате экспериментальных исследований установлено, что наилучшими материалами для коалесценции являются крупнозернистые коалесцирующие гидрофобные загрузки с повышенной скоростью фильтрации, которые работают в режиме саморегенерации. При этом повышается глубина очистки, продолжительность процесса отстаивания сокращается в 2 раза и более.

Ключевые слова: нефтепромысловые сточные воды, коалесцирующая загрузка, коалесцирующая насадка, предварительная обработка, фракционный состав, фильтрация, саморегенерация.

СПИСОК ЛИТЕРАТУРЫ

- Урмитова Н. С. Интенсификация процессов очистки нефтесодержащих сточных вод на основе применения гранулированных коалесцирующих материалов: Дисс. … канд. техн. наук. – Казань, КИСИ, 1993. 251 с.

- Адельшин А. Б., Урмитова Н. С. Использование гидродинамических насадок с крупнозернистой загрузкой для интенсификации очистки нефтесодержащих сточных вод. – Казань, КГАСУ, 1997. 249 с.

- Адельшин А. Б., Адельшин А. А., Урмитова Н. С. Новые технологические и технические решения установок очистки нефтепромысловых сточных вод на основе применения закрученных потоков // Известия КГАСУ. 2010. С. 197–205.

- Урмитова Н. С., Абитов Р. Н., Хисамеева Л. Р., Низамова А. Х. Оценка сил, способствующих разрушению частиц нефти в коалесцирующей насадке // Известия КГАСУ. 2015. № 2 (32). С. 226–230.

- Урмитова Н. С., Абитов Р. Н., Хисамеева Л. Р., Низамова А. Х. Математическое моделирование процессов коалесценции капель нефти в коалесцирующих насадках в крупнозернистых загрузках // Известия КГАСУ. 2015. № 4 (34). С. 248–252.

WASTEWATER TREATMENT

Urmitova N. S., Abitov R. N., Nizamova A. Kh., Khabibullin R. R. The use of coarse coalescent materials in the units for oil field water treatment 20

N. S. URMITOVA1, R. N. ABITOV2, A. Kh. NIZAMOVA3, R. R. KhABIBULLIN4

1 Urmitova Naziia Salikhovna, Ph. D. (Engineering), Associate Professor, «Water Supply and Wastewater Disposal» Department, Kazan State University of Architecture and Civil Engineering

1 Zelenaia St., 420043, Kazan, Russian Federation, tel.: +7 (843) 510-46-97, e-mail: kgasu.viv@gmail.com

2 Abitov Runar Nazilovich, Ph. D. (Education), Head of «Water Supply and Wastewater Disposal» Department, Kazan State University of Architecture and Civil Engineering

1 Zelenaia St., 420043, Kazan, Russian Federation, tel.: +7 (843) 510-46-97, e-mail: kgasu.viv@gmail.com

3 Nizamova Aida Khanifovna, Senior Lecturer, «Water Supply and Wastewater Disposal» Department, Kazan State University of Architecture and Civil Engineering

1 Zelenaia St., 420043, Kazan, Russian Federation, tel.: +7 (843) 510-46-97, e-mail: kgasu.viv@gmail.com

4 Khabibullin Rafil' Rafisovich, Engineer, Production Technology Department, «Zhilishche i Komfort» Management Company

8 Akademika Glushko St., 420100, Kazan, Russian Federation, tel.: +7 (843) 221-31-50, e-mail: info@ukgik.ru

The Republic of Tatarstan is a federal subject of Russia with high technology and economic level including petrochemical, oil extraction and oil refining industries. At the oil extraction facilities big amounts of oily water are generated. Reuse of this water for oil reservoir flooding to improve the production rate is an efficient method of utilization. Before the injection oil and mechanical admixtures must be removed from wastewater. This is provided by sedimentation method. To enhance the process wastewater pretreatment is used. Coalescence process with the use of granulated coalescent porous media is one of the most efficient methods. To enhance the treatment process granulated coalescent materials based on polymers and expanded clay were developed. As a result of experimental studies it was concluded that coarse hydrophobic media with increased filtration rate that work in self-regeneration mode is the best material for coalescence. Herewith the purification level is improved and the duration of sedimentation process is cut by half and more.

Key words: oil field water, coalescent media, coalescent nozzle, pretreatment, grain particle size, filtration, self-regeneration.

REFERENCES

- Urmitova N. S. Intensifikatsiia protsessov ochistki neftesoderzhashchikh stochnykh vod na osnove primeneniia granulirovannykh koalestsiruiushchikh materialov [Enhancement of oil field water treatment on the basis of the use of granulated coalescent materials: Ph. D. thesis in Engineering Science. Kazan, KISI Publ., 1993, 251 p.].

- Adel'shin A. B., Urmitova N. S. Ispol'zovanie gidrodinamicheskikh nasadok s krupnozernistoi zagruzkoi dlia intensifikatsii ochistki neftesoderzhashchikh stochnykh vod [The use of hydrodynamic nozzles with coarse media for the enhancement of oily wastewater treatment. Kazan, KGASU Publ., 1997, 249 p.].

- Adel'shin A. B., Adel'shin A. A., Urmitova N. S. [Advanced process and technical designs of the units for oil field water treatment on the basis of swirling flow use]. IzvestiiaKGASU, 2010, pp. 197–205. (In Russian).

- Urmitova N. S., Abitov R. N., Khisameeva L. R., Nizamova A. Kh. [Evaluation of the forces facilitating the destruction of particles in a coalescent nozzle]. IzvestiiaKGASU, 2015, no. 2 (32), pp. 226–230. (In Russian).

- Urmitova N. S., Abitov R. N., Khisameeva L. R., Nizamova A. Kh. [Mathematical modeling of the process of oil drops coalescence in coalescent nozzles in coarse media]. IzvestiiaKGASU, 2015, no. 4 (34), pp. 248–252. (In Russian).

УДК 628.312

Кофман В. Я. Химико-информационная разработка сточных вод (обзор) 26

В. Я. КОФМАН*

* Кофман Владимир Яковлевич, старший научный сотрудник, Всероссийский институт научной и технической информации Российской академии наук

125190, Россия, Москва, ул. Усиевича, 20, тел.: (499) 155-43-08, e-mail: kofman16@mail.ru

Научная дисциплина «Химико-информационная разработка сточных вод» возникла и стала быстро развиваться в начале 2000-х годов в ответ на запрос о создании каналов получения информации о потреблении запрещенных наркотических и фармацевтических препаратов широкого спектра, о воздействии токсических веществ, о ряде показателей состояния здоровья населения и его численности на исследуемой территории. В сравнении с традиционными методами анкетирования и социолого-эпидемиологических исследований, предполагающих сбор статистических данных, обработку медицинской документации, получение информации по производству и реализации соответствующих препаратов, рассматриваемый подход имеет некоторые преимущества и позволяет организовать непрерывный контроль практически в реальном масштабе времени. Кроме того, удается преодолеть ряд этических проблем, возникающих при использовании некоторых практикуемых методов исследования. Сущность метода заключается в измерении на входе очистных сооружений концентраций активных веществ исследуемых препаратов и/или их метаболитов, попадающих в систему канализации в результате экскреции из организма человека, и применении методики обработки этих данных для определения уровня потребления медицинских или наркотических препаратов населением, проживающим на территории, обслуживаемой данной канализационной сетью. Аналогично может быть определена степень подверженности населения воздействию загрязняющих веществ. Полученные в ряде стран данные с использованием рассматриваемого подхода соответствуют результатам традиционных исследований, а в некоторых случаях удачно их дополняют. Предполагается, что значимость и эффективность метода будут возрастать, в том числе в условиях модернизации канализационных сетей.

Ключевые слова: сточные воды, наркотические и фармацевтические препараты, токсические вещества, система канализации, централизованные очистные сооружения, методика обратного вычисления.

Kofman V. Ia. Chemical information study of wastewater (review) 26

V. Ia. KOFMAN*

* Kofman Vladimir Iakovlevich, Senior Research Fellow, All-Russian Institute of Scientific and Technical Information, Russian Academy of Sciences

20 Usuevicha St., 125190, Moscow, Russian Federation, tel.: +7 (499) 155-43-08, e-mail: kofman16@mail.ru

The research discipline «Chemical information study of wastewater» has originated and made rapid strides since the beginning of 2000-ies in response to the demand of developing the channels of acquiring the information on the use of broad spectrum of banned narcotics and pharmaceuticals, on the effect of toxic substances, on some health indicators of the population and its size inside the territory under the study. Compared to the traditional methods of questioning and social-epidemiologic studies that imply the compilation of statistics, study of medical reports, acquisition of the information on the production and sale of the relevant medications the considered approach has certain advantages and provides for establishing continuous monitoring almost on a real-time basis. The method includes measuring the concentrations of active substances and/or metabolites of the medications studied that enter the sewer as a result of the excretion from the human organism and using the method of this data processing to determine the level of consumption of medications or narcotics by the population living on the territory served by the sewer network. Similarly the level of the population exposure to the impact of pollutants can be determined. The data obtained in some countries with the use of the considered approach corresponds to the results of the traditional studies, and, in some cases is a successful supplement. It is supposed that the significance and efficiency of the method will grow as well as under the conditions of the sewer network upgrade.

Key words: wastewater, narcotics and pharmaceuticals, toxic substances, sewerage system, public wastewater treatment facilities, back calculations method.

REFERENCES

- Zucatto E., Chiabrando C., Castigliony, et al. Estimating community drug abuse by wastewater analysis. Environmental Health Perspective, 2008, v. 116, no. 8, pp. 1027–1032.

- Ort C., Lawrence M. G., Reungoat J., et al. Sampling for PPCPs in wastewater systems: comparison of different sampling modes and optimization strategies. Environmental Science and Technology, 2010, v. 44, no. 16, рр. 6289–6296.

- Daughton C. G. Real-time estimation of small-area populations with human biomarkers in sewage. Science of the Total Environment, 2012, v. 414, pp. 6–21.

- Baker D. R., Kasprzyk-Hordern B. Critical evaluation of methodology commonly used in sample collection, storage and preparation for the analyses of pharmaceuticals and illicit drugs in surface water and wastewater by solid phase extraction and liquid chromatography-mass spectrometry. Journal of Chromatography A, 2011, v. 44, pp. 8036–8059.

- Gao J., O'Brien J. W., Lai F. Y., et al. Could wastewater analysis be a useful tool for China? Journal of Environmental Sciences, 2015, v. 27, pp. 70–79.

- Van Nuijs A. L. N., Mougel J.-F. Tarcomnicu I., et al. Sewage epidemiology – a real-time approach to estimate the consumption of illicit drugs in Brussels, Belgium. Environmental International, 2011, v. 37, no. 3, pp. 612–621.

- O'Brien J. W., Thai P. K., Eaglesham G., et al. A model to estimate the population contributing to the wastewater using samples collected on census day. Environmental Science and Technology, 2014, v. 48, pp. 517–525.

- O'Brien J. W., Banks A. P. W., Novic A. J., et al. Impact of in-sewer degradation of pharmaceuticals and personal care products (PPCPs) population markers on a populational model. Environmental Science and Technology, 2017, v. 51, pp. 3816–3823.

- Chen C., Kostakis G., Gerber J. P., et al. Towards finding a population biomarker for wastewater epidemiology study. Science of the Total Environment, 2014, v. 481, pp. 621–628.

- Castiglioni S., Bijlsma L., Covaci A., et al. Evaluation of uncertainties associated with the determination of community drug use through the measurement of sewage drug biomarkers. Environmental Science and Technology, 2013, v. 47, no. 3, pp. 1452–1460.

- Alexander L. N., van Nuijs A. L. N., Castiglioni S., et al. Illicit drug consumption estimations derived from wastewater analysis: A critical review. Science of the Total Environment, 2011, v. 409, pp. 3564–3577.

- Thomas K. V., Bijlsma L., Castiglioni S., et al. Comparison illicit drug use in 19 European cities through sewage analysis. Science of the Total Environment, 2012, v. 432, pp. 432–439.

- Gatidou G., Kinyua J., van Nuijs A. L. N., et al. Drugs of abuse and alcohol consumption among different groups of population on the Greek island of Lesvos through sewage-based epidemiology. Science of the Total Environment, 2016, v. 563–564, pp. 633–640.

- Daughton C. G. Using biomarkers in sewage to monitor community-wide human health: isoprostanes as conceptual prototype. Science of the Total Environment, 2012, v. 424, pp. 16–38.

- Gonzalez-Marino I., Rodil R., Barrio I., et al. Wastewater-based epidemiology as a new tool for estimating population exposure to phthalate plasticizers. Environmental Science and Technology, 2017, v. 51, no. 7, pp. 3902–3910.

- Liu W.-R., Yang Y.-Y., Liu Y.-S., et al. Biocides in wastewater treatment plants: Mass balance analysis and pollution load estimation. Journal of Hazardous Materials, 2017, v. 329, pp. 310–320.

- Massoud M. A., Chami G., Al-Hindi M., et al. Assessment household disposal of pharmaceuticals in Lebanon: Management options to protect water quality and public health. Environmental Management, 2016, v. 57, pp. 1125–11374.

- Bu Q., Wang Wang B., Huang J., et al. Estimating the use of antibiotics for human across China. Chemosphere, 2016, v. 144, pp. 1384–1390.

- Bu Q., Shi X., Yu G., et al. Pay attention to non-wastewater emission pathways of pharmaceuticals into environments. Chemosphere, 2016, v. 16, pp. 515–518.

- Bound J. P., Voulvoulis N. Household disposal of pharmaceuticals as a pathway for aquatic contamination in the United Kingdom. Environmental Health Perspective, 2005, v. 113, pp. 1705–1711.

- Massoud M. A., Chami G., Al-Hindi M., et al. Assessment of household disposal of pharmaceuticals in Lebanon: Management options to protect water quality and public health. Environmental Management, 2016, v. 57, pp. 1125–1137.

- Peng X., Qu W., Wang C., et al. Occurence and ecological potential of pharmaceuticals and personal care products in groundwater and reservoirs in the vicinity of municipal landfills in China. Science of the Total Environment, 2014, v. 490, pp. 889–892.

- Postigo C., de Alda M. L., Barcelo D. Evaluation of drugs of abuse use and trends in a prison through wastewater analysis. Environmental International, 2011, v. 37, pp. 49–55.

- Zeeman G., Kujawa K., de Mes T., et al. Anaerobic treatment as a core technology for energy, nutrients and water recovery from source-separated domestic waste(water). Water Science and Technology, 2008, v. 57, p. 1207–1212.

ОЧИСТКА ПОВЕРХНОСТНОГО СТОКА

УДК 628.31:581.55

Щукин И. С. Исследование процессов очистки поверхностных сточных вод от нефтепродуктов и тяжелых металлов на фитофильтрах 35

И. С. ЩУКИН*

* Щукин Игорь Сергеевич, старший преподаватель кафедры «Теплогазоснабжение, вентиляция и водоснабжение, водоотведение», Пермский национальный исследовательский политехнический университет

614990, Россия, г. Пермь, Комсомольский проспект, 29, тел.: (912) 986-70-03, e-mail: shchukin-is@yandex.ru

В мировой практике очистки поверхностных сточных вод с урбанизированных территорий все большее распространение получают биоинженерные сооружения, в том числе фитофильтры. Применение фитофильтров в условиях умеренного климатического пояса имеет ограничения, связанные со снижением эффективности очистки в периоды околонулевых температур ввиду замедления биохимических процессов, происходящих в растениях и почвенных микроорганизмах. Предложено техническое решение описанной проблемы, которое заключается в добавлении в состав фильтрующей загрузки материалов, обладающих сорбционными и ионообменными свойствами (торфа и цеолита). Проведены исследования эффективности очистки модельного раствора поверхностных сточных вод от нефтепродуктов и тяжелых металлов (свинца, меди, алюминия, железа) на пилотной лабораторной установке фитофильтрования с использованием высших растений: тростника обыкновенного (Phragmites commúnis), рогоза широколистного (Týpha latifólia) и ириса болотного (Iris pseudacorus). Эффективность очистки от нефтепродуктов составила 95,5–98,9%, от тяжелых металлов – 66–99,3%. Установлено, что в вегетационный период под действием высших растений и ризосферной микрофлоры происходит частичная фиторегенерация фильтрующей загрузки от задержанных нефтепродуктов и тяжелых металлов. Экспериментально определено, что эффективность фиторегенерации высшими растениями от нефтепродуктов уменьшается в ряду: тростник обыкновенный – ирис болотный – рогоз широколистный; от тяжелых металлов: ирис болотный – тростник обыкновенный.

Ключевые слова: поверхностные сточные воды, нефтепродукты, тяжелые металлы, фитофильтр, фиторегенерация, дождевые сады.

СПИСОК ЛИТЕРАТУРЫ

- Щукин И. С., Мелехин А. Г. Качественный состав поверхностного стока с территории г. Перми // Вестник ПНИПУ. Урбанистика. 2012. № 4. С. 110–118.

- Чечевичкин В. Н., Ватин Н. И. Особенности состава и очистки поверхностного стока крупных городов // Инженерно-строительный журнал. 2014. № 6. С. 67–74.

- Щукин И. С., Мелехин А. Г. Анализ существующих биоинженерных сооружений очистки поверхностного стока и возможности их применения в условиях Западного Урала // Вестник ПНИПУ. Строительство и архитектура. 2013. № 2. С. 40–51.

- Ильин В. Б. Тяжелые металлы в системе «почва–растения». – Новосибирск: Наука, 1991. 151 с.

- Наумова Л. Б., Горленко Н. П., Отмахова З. И., Мокроусов Г. М. Использование торфов Томской области при очистке сточных вод от ионов тяжелых металлов и нефтепродуктов // Химия в интересах устойчивого развития. 1997. № 5. С. 609–611.

- Касицкая Л. В., Саркисов Ю. С., Горленко Н. П., Копаница Н. О., Кудяков А. И. Торфяные ресурсы Томской области и пути их использования в строительстве. – Томск: SST Издательство, 2007. 290 с.

- Короткова Ю. А. Использование торфа и торфогеля как органического удобрения // Молодой ученый. 2015. № 1. С. 158–161.

- Кельцев Н. В. Основы адсорбционной техники. – М.: Химия, 1984. С. 85–87.

- Обуздина М. В. Природные и модифицированные цеолиты как адсорбенты нефтепродуктов из промышленных сточных вод // Вестник Иркутского государственного технического университета. 2010. № 4 (44). С. 104–110.

- Каратаев О. Р., Новиков В. Ф., Шамсутдинова З. Р. Очистка сточных вод цеолитсодержащими породами // Вестник Казанского технологического университета. 2014. Т. 17. № 15. С. 169–174.

- Ватин Н. И., Панкова Г. А., Леонов Л. В., Пробирский М. Д., Рублевская О. Н., Чечевичкин А. В., Якунин Л. А. Тестовая эксплуатация фильтра ФОПС® с природным цеолитом для очистки загрязненного инфильтратом поверхностного стока // Водоснабжение и санитарная техника. 2017. № 9. С. 39–49.

- Корецкий Д. С., Игнатова А. Ю. Изучение влияния цеолита Пегасского месторождения на рост растений // Вестник Кузбасского государственного технического университета. 2010. № 2. С. 92–95.

- Титов А. Ф., Казнина Н. М., Таланова В. В. Тяжелые металлы и растения. – Петрозаводск, Карельский научный центр РАН, 2014. 194 с.

- Степанова А. Ю., Орлова Е. В. Оценка эффективности использования растений Райграса (Lolium Perenne L.) и люцерны (Medicago Sativa L.) для фиторемедиации нефтезагрязненного грунта // Ученые записки Орловского государственного университета. Естественные, технические и медицинские науки. 2012. № 3. С. 327–330.

- Щукин И. С., Ручкинова О. И. Многокомпонентная фильтрующая загрузка для фитофильтров очистки поверхностных сточных вод // Вестник ПНИПУ. Прикладная экология и урбанистика. 2017. № 1. С. 105–115.

- Ватин Н. И., Греков М. А., Леонов Л. В., Пробирский М. Д., Рублевская О. Н., Чечевичкин А. В., Якунин Л. А. Результаты тестовой эксплуатации фильтра ФОПС® для очистки ливневого стока с селитебной территории Санкт-Петербурга // Водоснабжение и санитарная техника. 2017. № 1. С. 58–65.

- Методические указания по определению тяжелых металлов в почвах сельхозугодий и продукции растениеводства. – М., ЦИНАО, 1992. 61 с.

- Пат. 2540620, РФ. МПК C 02 F9/14, C 02 F3/32, C 02F1/28, B 01D24/00. Устройство для очистки поверхностных сточных вод / Щукин И. С., Мелехин А. Г. // Изобретения. Полезные модели. 2015. № 4.

SURFACE RUNOFF TREATMENT

Shchukin I. S. Study of oil products and heavy metals removal from surface runoff in phytofilters 35

I. S. SHCHUKIN*

* Shchukin Igor' Sergeevich, Senior Lector, «Heat Supply, Ventilation and Water Supply, Wastewater Disposal» Department, Perm National Research Polytechnic University

29 Komsomol’skii Ave., 614990, Perm, Russian Federation, tel.: +7 (912) 986-70-03, e-mail: shchukin-is@yandex.ru

Internationally the use of bioengineered facilities including phytofilters in the treatment of surface runoff from urban lands is gaining ground. The use of phytofilters in moderate climate belts has some restrictions related to the decline in treatment efficiency during the periods of near-zero temperatures because of the retardation of biochemical processes in plants and soil microorganisms. A technical solution of the described problem is proposed that consists in adding materials with sorption and ion-exchange properties (peat and zeolite) into the filter media. The efficiency of removing oil products and heavy metals (lead, copper, aluminium, iron) from the simulated solution of surface runoff in a pilot laboratory phytofiltration plant with the use of higher plants: common reed grass (Phragmites commúnis), mace reed (Týpha latifólia) and Iris pseudacorus was studied. The efficiency of removing oil products was 95.5–98.9%, and that of heavy metals – 66–99.3%. It was stated that during the vegetation period partial phytoregeneration of the filtration media from the trapped oil products and heavy metals occurs under the effect of higher plants and rhizospheric microflora. By experiment it was determined that the efficiency of phytoregeneration from oil products decreases in series: common reed grass – Iris pseudacorus – mace reed; from heavy metals: Iris pseudacorus – common reed grass.

Key words: surface runoff, oil products, heavy metals, phytofilter, phytoregeneration, rain gardens.

REFERENCES

- Shchukin I. S., Melekhin A. G. [Qualitative composition of surface runoff from the territory of Perm city]. Vestnik PNIPU. Urbanistika, 2012, no. 4, pp. 110–118. (In Russian).

- Chechevichkin V. N., Vatin N. I. [Specific features of the composition and treatment of surface runoff in big cities]. Inzhenerno-Stroitel'nyi Zhurnal, 2014, no. 6, pp. 67–74. (In Russian).

- Shchukin I. S., Melekhin A. G. [Analysis of the existing bioengineered facilities for surface runoff treatment and the potential of using under the conditions of the West Urals]. Vestnik PNIPU. Stroitel'stvo i Arkhitektura, 2013, no. 2, pp. 40–51. (In Russian).

- Il'in V. B. Tiazhelye metally v sisteme «pochva–rasteniia» [Heavy metals in the «soil-plants» system. Novosibirsk, Nauka Publ., 1991, 151 p.].

- Naumova L. B., Gorlenko N. P., Otmakhova Z. I., Mokrousov G. M. [The use of peat from the Tomsk Area in removing heavy metal ions and oil products from wastewater]. Khimiia v Interesakh Ustoichivogo Razvitiia, 1997, no. 5, pp. 609–611. (In Russian).

- Kasitskaia L. V., Sarkisov Iu. S., Gorlenko N. P., Kopanitsa N. O., Kudiakov A. I. Torfianye resursy Tomskoi oblasti i puti ikh ispol'zovaniia v stroitel'stve [Peat resources in the Tomsk Area and possible use in the construction. Tomsk, SST Publ., 2007, 290 p.].

- Korotkova Iu. A. [The use peat and peat gel as organic fertilizers]. Molodoi Uchenyi, 2015, no. 1, pp. 158–161. (In Russian).

- Kel'tsev N. V. Osnovy adsorbtsionnoi tekhniki [Fundamentals of adsorption technics. Moscow, Khimiia Publ., 1984, pp. 85–87].

- Obuzdina M. V. [Natural and modified zeolites as adsorbents of oil products from industrial wastewater]. Vestnik Irkutskogo Gosudarstvennogo Tekhnicheskogo Universiteta, 2010, no. 4 (44), pp. 104–110. (In Russian).

- Karataev O. R., Novikov V. F., Shamsutdinova Z. R. [Wastewater treatment with zeolite containing stones]. Vestnik Kazanskogo Tekhnologicheskogo Universiteta, 2014, v. 17, no. 15, pp. 169–174. (In Russian).

- Vatin N. I., Pankova G. A., Leonov L. V., Probirskii M. D., Rublevskaia O. N., Chechevichkin A. V., Iakunin L. A. [Test operation of FOPS® filter with natural zeolite for infiltrate polluted surface runoff treatment]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2017, no. 9, pp. 39–49. (In Russian).

- Koretskii D. S., Ignatova A. Iu. [Study of the Pegasskoe deposit zeolite effect on the plant growth]. Vestnik Kuzbasskogo Gosudarstvennogo Tekhnicheskogo Universiteta, 2010, no. 2, pp. 92–95. (In Russian).

- Titov A. F., Kaznina N. M., Talanova V. V. Tiazhelye metally i rasteniia [Heavy metals and plants. Petrozavodsk, Karel'skii nauchnyi tsentr RAN Publ., 2014, 194 p.].

- Stepanova A. Iu., Orlova E. V. [Assessment of the efficiency of using ryegrass plants (Lolium Perenne L.) and lucerne (Medicago Sativa L.) for phytomediation of oil polluted soils]. Uchenye zapiski Orlovskogo Gosudarstvennogo Universiteta. Estestvennye, Tekhnicheskie i Meditsinskie Nauki, 2012, no. 3, pp. 327–330. (In Russian).

- Shchukin I. S., Ruchkinova O. I. [Multicomponent filter media for phytofilters for surface runoff treatment]. Vestnik PNIPU. Prikladnaia Ekologiia i Urbanistika, 2017, no. 1, pp. 105–115. (In Russian).

- Vatin N. I., Grekov M. A., Leonov L. V., Probirskii M. D., Rublevskaia O. N., Chechevichkin A. V., Iakunin L. A. [Results of the test operation of FOPS® filter for treatment of stormwater runoff from residential areas in Saint-Petersburg]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2017, no. 1, pp. 58–65. (In Russian).

- Metodicheskie ukazaniia po opredeleniiu tiazhelykh metallov v pochvakh sel'khozugodii i produktsii rastenievodstva [Methodological guidelines on determining heavy metals in agricultural soils and plant products. Moscow, TSINAO Publ., 1992, 61 p.].

- Shchukin I. S., Melekhin A. G. [Pat. 2540620, RF. IPC C 02 F9/14, C 02 F3/32, C 02F1/28, B 01D24/00. Facility for surface runoff treatment]. Izobreteniia. Poleznye Modeli, 2015, no. 4. (In Russian).

ПРОЕКТИРОВАНИЕ СИСТЕМ ВОДОСНАБЖЕНИЯ И ВОДООТВЕДЕНИЯ

УДК 628.218

- Чупин Р. В. Оптимизация перспективных схем развития систем водоотведения в условиях ограниченного финансирования 44

Р. В. ЧУПИН*

* Чупин Роман Викторович, кандидат технических наук, старший научный сотрудник, кафедра «Городское строительство и хозяйство», Институт архитектуры и строительства, Иркутский национальный исследовательский технический университет

664074, Россия, г. Иркутск, ул. Лермонтова, 83, тел.: (925) 941-36-70, e-mail: ch-r-v@mail.ru

Переход к рыночным отношениям определил новую для нашей страны технологию управления развитием городских инженерных систем. Эту технологию можно представить в виде двух этапов. Первый этап – разработка схем развития систем водоснабжения и водоотведения, второй – реализация этих схем на основе инвестиционных программ предприятий коммунального комплекса. В инвестиционных программах формируется финансовое обеспечение развития и реконструкции систем водоотведения за счет инвестиционной составляющей в тарифе, платы за подключение для вновь вводимых в строй объектов капитального строительства и целевого финансирования по отдельным государственным и муниципальным программам, займам и кредитам. При таком подходе определяющими становятся инвестиции и их ограниченность по этапам и периодам развития системы водоотведения. В связи с этим возникают новые проблемы и задачи, связанные с рациональным распределением этих инвестиций в строительство новых и реконструкцию существующих объектов и сооружений систем водоотведения. На основе разработанных моделей и методов для обоснования структуры и параметров систем водоотведения предлагается методика формирования и оптимизации вариантов развития системы водоотведения в условиях ограниченных инвестиций.

Ключевые слова: оптимальное управление развитием систем водоотведения, избыточная схема, количественные показатели, надежность, сейсмостойкость, экологическая безопасность, ограниченное финансирование.

СПИСОК ЛИТЕРАТУРЫ

- Храменков С. В., Орлов В. А., Харькин В. А. Оптимизация восстановления водоотводящих сетей. – М.: Стройиздат, 2002. 185 с.

- Саломеев В. П. Реконструкция инженерных систем и сооружений водоотведения. – М.: Издательство АСВ, 2009. 192 с.

- Кристофидес Н. Теория графов. Алгоритмический подход. – М.: Мир, 1978. 429 c.

- Чупин Р. В. Оптимизация развивающихся систем водоотведения. – Иркутск: Издательство ИрГТУ, 2015. 418 с.

- Гогина Е. С., Гуринович А. Д. Применение методики LCC для оценки эффективности проектов сооружений очистки сточных вод // Водоснабжение и санитарная техника. 2016. № 9. С. 36–41.

- Составление технико-экономической части проектов внеплощадочных систем водоснабжения и канализации: Справочное пособие к СНиП / Союзводоканалпроект. – М.: Стройиздат, 1991. 80 с.

- Сайритдинов С. Ш. Гидравлика систем водоснабжения и водоотведения: Учебное пособие. – М.: Издательство АСВ, 2012. 352 с.

- Алексеев М. И., Ермолин Ю. А. Надежность сетей и сооружений систем водоотведения: Учебное пособие. – М.: Издательство АСВ, 2015. 200 с.

- Чупин Р. В., Горьков Е. С. Повышение надежности и сейсмостойкости самотечных систем водоотведения // Водоснабжение и санитарная техника. 2015. № 6. С. 62–69.

- Гехман А. С., Зайнетдинов Х. Х. Расчет, конструирование и эксплуатация трубопроводов в сейсмических районах. – М.: Стройиздат, 1988. 184 с.

- Чупин Р. В., Нгуен Т. А. Оптимальная реконструкция систем водоотведения // Водоснабжение и санитарная техника. 2015. № 2. С. 58–66.

DESIGNING WATER AND WASTEWATER SYSTEMS

Chupin R. V. Optimization of the prospective plans of water supply system development under the tight financing conditions 44

R. V. CHUPIN*

* Chupin Roman Viktorovich, Ph. D. (Engineering), Senior Research Worker, «Urban Development and Public Utilities» Department, Architecture and Civil Engineering Institute, Irkutsk National Research Technical University

83 Lermontova St., 664074, Irkutsk, Russian Federation, tel.: +7 (925) 941-36-70, e-mail: ch-r-v@mail.ru

The transition to market relations determined a new for our country technology of the urban utility systems management. This technology can be presented in two stages. The first stage is the development of the water supply and wastewater disposal plans; the second one – is the implementation of these plans on the basis of the investment programs of the public utility sector. The investment programs are shaping the financial support of the development and upgrade of wastewater disposal systems by means of the investment component in the tariff; charges for connecting newly built capital construction projects and targeted financing from separate state and municipal programs, loans and credits. Under this approach the determinants are the investments and their limitation in stages and wastewater disposal system development periods. In connection with this new problems and challenges arise related to the efficient allocation of these investments in the construction of new and upgrade of the existing water and wastewater projects. Based on the developed models and methods of substantiating the structure and parameters of wastewater disposal systems a method of shaping and optimizing the options of wastewater disposal system development under the tight financing conditions is proposed.

Key words: optimal management of water supply and wastewater disposal system development, redundant circuit, quantitative indicators, integrity, seismic resistance, environmental safety, tight financing.

REFERENCES

1.	Khramenkov S. V., Orlov V. A., Khar'kin V. A. Optimizatsiia vosstanovleniia vodootvodiashchikh setei [Optimization and rehabilitation of sewers. Moscow, Stroiizdat Publ., 2002, 185 p.].

2.	Salomeev V. P. Rekonstruktsiia inzhenernykh sistem i sooruzhenii vodootvedeniia [Reconstruction of utility systems and wastewater disposal facilities. Moscow, ASV Publ., 2009, 192 p.].

3.	Kristofidis N. Teoriia grafov. Algoritmicheskii podkhod [Theory of graphs. Algorithmic approach. Moscow, Mir Publ., 1978, 429 p.].

4.	Chupin R. V. Optimizatsiia razvivaiushchikhsia sistem vodootvedeniia [Optimization of the developing wastewater disposal systems. Irkutsk, IrGTU Publ., 2015, 418 p.].

5.	Gogina E. S., Gurinovich A. D. [The use of LCC method in evaluating the efficiency of investment projects of wastewater treatment facilities] Vodosnabzhenie i Sanitarnaia Tekhnika, 2016, no. 9, pp. 36–41. (In Russian).

6.	Sostavlenie tekhniko-ekonomicheskoi chasti proektov vneploshchadochnykh sistem vodosnabzheniia i kanalizatsii: Spravochnoe posobie k SNiP [Drawing up the technoeconomic part of the off-site water supply and wastewater disposal system projects. Reference book to SNiP / Soiuzvodokanalproekt. Moscow, Stroiizdat Publ., 1991, 80 p.].

7.	Sairitdinov S. Sh. Gidravlika sistem vodosnabzheniia i vodootvedeniia [Water supply and wastewater disposal system hydraulics. Study guide. Moscow, ASV Publ., 2012, 352 p.].

8.	Alekseev M. I., Ermolin Iu. A. Nadezhnost' setei i sooruzhenii sistem vodootvedeniia [Wastewater disposal networks and facilities integrity. Study guide. Moscow, ASV Publ., 2015, 200 p.].

9.	Chupin R. V., Gor'kov E. S. [Improvement of the integrity and seismic resistance of gravity sewers]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2015, no. 6, pp. 62–69. (In Russian).

10.	Gekhman A. S., Zainetdinov Kh. Kh. Raschet, konstruirovanie i ekspluatatsiia truboprovodov v seismicheskikh raionakh [Calculation, design and operation of pipelines in earthquake areas. Moscow, Stroiizdat Publ., 1988, 184 p.].

11.	Chupin R. V., Nguen T. A. [Optimal upgrade of sewers]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2015, no. 2, pp. 58–66. (In Russian).

ЭНЕРГОСБЕРЕЖЕНИЕ

УДК 628.1.2:658.26.004.18

Усачев А. П. Управление параллельной работой центробежных насосов 55

А. П. УСАЧЕВ*

* Усачев Алексей Павлович, кандидат технических наук, технический директор, ООО «Сибирь-мехатроника»

630087, Россия, г. Новосибирск, а/я 169, тел.: (383) 399-00-55, e-mail: usachev@sibmech.ru

Рассматриваются проблемы, связанные с токовой загрузкой насосных агрегатов при их параллельной работе (один – с частотным управлением, другой – без частотного управления). В традиционных схемах управления (без частотного регулирования) проблема решается путем дросселирования каждого насоса с выравниванием токовой загрузки их приводных электродвигателей. Эта функция выполняется, как правило, оператором в ручном режиме. На основании проведенного анализа разработан алгоритм управления насосами, обеспечивающий их безопасную работу в рабочей зоне и максимальную энергоэффективность. Предлагается производить контролируемое дросселирование насоса без частотного регулирования путем контроля положения рабочей точки насоса с частотным регулированием на границе рабочей зоны. Для обеспечения безаварийной работы насосной станции при аварийной остановке насоса с частотным регулированием рекомендуется систему управления насосом без частотного регулирования перестроить на работу автоматического поддержания давления с помощью дросселирования. Для реализации данного алгоритма предлагается использование специализированного технологического контроллера с достаточной вычислительной мощностью (типа СТК 500) и блоки серии СР 200.

Ключевые слова: центробежный насос, параллельная работа, частотное регулирование, дросселирование, энергосбережение.

СПИСОК ЛИТЕРАТУРЫ

- Багаев Ю. Г., Карпов Н. В., Усачев А. П. Параллельная работа насоса с частотно-регулируемым электроприводом // Водоснабжение и санитарная техника. 2014. № 4. С. 38–41.

- Усачев А. П., Гордейчик А. В. Особенности частотного регулирования насосами с учетом рабочего диапазона: Материалы Международного форума «Вода: экология и технология» – «ЭКВАТЭК–2014», Москва, МВЦ «Крокус Экспо», 4–5 июня 2014 г.

- Лезнов Б. С. Энергосбережение и регулируемый привод в насосных и воздуходувных установках. – М.: Энергоатомиздат, 2006. 360 с.

ENERGY CONSERVATION

Usachev A. P. Control of centrifugal pump parallel operation 55

A. P. USACHEV*

* Usachev Aleksei Pavlovich, Ph. D. (Engineering), Technical Director, «Sibir’-Mekhatronika» LLC

P. O. Box 169, 630087, Novosibirsk, Russian Federation, tel.: +7 (383) 399-00-55, e-mail: usachev@sibmech.ru

The problems related to the cable capacity of pumping units during their parallel operation (one with variable-frequency control, another one – without variable-frequency control) are considered. In the traditional control schemes (without variable-frequency control) the problem is solved by throttling of each pump with cable capacity levelling of their drive motors. This function is usually carried out by the operator in manual mode. Based on the conducted analysis an algorithm of pump control was developed that provided for their safe operation in the working area and maximum energy efficiency. It is proposed to carry out controlled throttling of the pump without variable-frequency control by controlling the position of the set point of the pump with variable-frequency control at the working area interface. To ensure failure-free operation of the pumping station in case of the pump with variable-frequency control emergency shutdown it is recommended to change the system of the pump without variable-frequency control for automated pressure maintaining with the help of throttling. To implement the given algorithm the use of a special process controller with the sufficient computing power (STK 500 type) and series SP 200 blocks is proposed.

Key words: centrifugal pump, parallel operation, variable-frequency control, throttling, energy conservation.

REFERENCES

- Bagaev Iu. G., Karpov N. V., Usachev A. P. [Parallel operation of pumps with variable-frequency drive]. Vodosnabzhenie i Sanitarnaia Tekhnika, 2014, no. 4, pp. 38–41. (In Russian).

- Usachev A. P., Gordeichik A. V. [Specific features of pump frequency control with account of the operational range]. Proceedings of International Forum «Water: Ecology and Technology» – «ECWATECH–2014», Moscow, «Crocus Expo» IEC, June 4–5, 2014. (In Russian).

- Leznov B. S. Energosberezhenie i reguliruemyi privod v nasosnykh i vozdukhoduvnykh ustanovkakh [Energy conservation and variable-speed drive in pumping units and air blowers. Moscow, Energoatomizdat Publ., 2006, 360 p.].

ТРУБОПРОВОДНЫЕ СИСТЕМЫ

УДК 621.644:621.643.2-034.13

Продоус О. А., Джанбеков Б. А. Трубы с полиуретановым покрытием для строительства Тебердинского магистрального группового водопровода 61

О. А. ПРОДОУС1, Б. А. ДЖАНБЕКОВ2

1 Продоус Олег Александрович, доктор технических наук, профессор, генеральный директор ООО «ИНКО-инжиниринг»

190005, Россия, Санкт-Петербург, Московский проспект, 37/1, литера А, тел.: (812) 318-55-62, e-mail: pro@enco.su

2 Джанбеков Борис Алиевич, президент Некоммерческой организации Фонд содействия реализации национальных программ «Эльбрус»

369200, Россия, Карачаево-Черкесская Республика, г. Карачаевск, ул. Орджоникидзе, 17, тел.: (928) 388-05-32, e-mail: bordjan@rambler.ru

Проблему дефицита питьевой воды в южных регионах России (на Северном Кавказе) можно решить путем строительства магистрального водопровода большого диаметра и большой протяженности для транспортирования воды из подземных артезианских источников, расположенных в Карачаево-Черкесской Республике. Проведен анализ современных эффективных, долговечных полимерных материалов для напорных трубопроводов, работающих в зоне с экстремальной сейсмичностью и имеющих высокий гидравлический потенциал. Показана экономическая эффективность использования труб из высокопрочного чугуна с полиуретановым внутренним покрытием при строительстве Тебердинского магистрального группового водопровода большого диаметра. Приведены удельные потери напора по длине водовода диаметром 500 мм, которые в 2,5 раза меньше удельных потерь напора в трубах из напорного полиэтилена того же диаметра.

Ключевые слова: дефицит питьевой воды, трубопровод, полимерные материалы, потери напора, энергопотребление насоса.

СПИСОК ЛИТЕРАТУРЫ

- Продоус О. А., Мурлин А. А., Иващенко В. В. Критерии выбора материалов труб для напорных трубопроводов коммунального и промышленного водоснабжения: Материалы X Международной научно-практической конференции «Техновод–2017». – Астрахань, 2017. С. 5–53.

- Продоус О. А. Таблицы для гидравлического расчета труб напорных из полиэтилена. Справочное пособие. – СПб.: Свое издательство, 2017. 240 с.

PIPELINE SYSTEMS

Prodous O. A., Dzhanbekov B. A. Pipes with polyurethane coating for the construction of the Teberda group water main 61

O. A. PRODOUS1, B. A. DZHANBEKOV2

1 Prodous Oleg Aleksandrovich, Doctor of Engineering, Professor, General Director, «ENCO-Engineering» LLC

Build. A, 37/1 Moskovskii Ave., 190005, St. Petersburg, Russian Federation, tel.: +7 (812) 318-55-62, e-mail: pro@enco.su

2 Dzhanbekov Boris Alievich, President, «Elbrus» National Programs Implementation Assistance Fund, Non-Profit Organization

17 Ordzhonikidze St., 369200, Karachaevsk, Karachay-Cherkessia Republic, Russian Federation, tel.: +7 (928) 388-05-32, e-mail: bordjan@rambler.ru

The problem of drinking water deficiency in the southern regions of Russia (at the North Caucasus) can be solved by the construction of a large-diameter and long water main for water transportation from the artesian sources located in the Karachay-Cherkessia Republic. The analysis of the advanced efficient durable polymer materials for pressure pipelines having the high hydraulic potential and operating in the zone of extreme seismicity was carried out. The economic efficiency of using ductile iron pipes with polyurethane inner coating in the construction of the Teberda group large-diameter water main is shown. The specific head losses along the length of a 500 mm water main are cited that are 2.5 times less than the specific head losses in pressure polyethylene pipes of the same diameter.

Key words: drinking water deficiency, pipeline, polymer materials, head loss, pump energy consumption.

REFERENCES

- Prodous O. A., Murlin A. A., Ivashchenko V. V. [Criteria of selecting pipe materials for pressure public and industrial water pipelines]. Proceedings of X International Scientific-practical Conference «Tekhnovod–2017». Astrakhan, 2017, pp. 5–53. (In Russian).

- Prodous O. A. Tablitsy dlia gidravlicheskogo rascheta trub napornykh iz polietilena [Tables for hydraulic calculation of pressure polyethylene pipes. Reference Book. St. Petersburg, Svoe Izdatel'stvo Publ., 2017, 240 p.].